## Cover page
T HR EL 11001 TI
Technical Information
SCADA Standard I/O Schedule
Version 2.0
Issue date: 25 February 2020
Superseded by TS 03863:0.00 24/11/2025

## Important message
T HR EL 11001 TI
SCADA Standard I/O Schedule
Version 2.0
Issue date: 25 February 2020
Important message
This document is one of a set of standards developed solely and specifically for use on Transport Assets (as defined in the Asset Standards Authority Charter). It is not suitable for any other purpose. The copyright and any other intellectual property in this document will at all times remain the property of the State of New South Wales (Transport for NSW). You must not use or adapt this document or rely upon it in any way unless you are providing products or services to a NSW Government agency and that agency has expressly authorised you in writing to do so. If this document forms part of a contract with, or is a condition of approval by a NSW Government agency, use of the document is subject to the terms of the contract or approval. To be clear, the content of this document is not licensed under any Creative Commons Licence. This document may contain third party material. The inclusion of third party material is for illustrative purposes only and does not represent an endorsement by NSW Government of any third party product or service. If you use this document or rely upon it without authorisation under these terms, the State of New South Wales (including Transport for NSW) and its personnel does not accept any liability to you or any other person for any loss, damage, costs and expenses that you or anyone else may suffer or incur from your use and reliance on the content contained in this document. Users should exercise their own skill and care in the use of the document. This document may not be current and is uncontrolled when printed or downloaded. Standards may be accessed from the Transport for NSW website at www.transport.nsw.gov.au

## Standard governance
T HR EL 11001 TI
SCADA Standard I/O Schedule
Version 2.0
Issue date: 25 February 2020
Standard governance
Owner: | Lead Electrical Engineer, Asset Standards Authority
Authoriser: | Chief Engineer, Asset Standards Authority
Approver: | Executive Director, Asset Standards Authority on behalf of the ASA Configuration
Control Board
Document history
Version | Summary of changes
1.0 | First issue, 28 June 2018.
2.0 | Second issue - updates to reflect new equipment requirements and the modification of
some existing equipment requirements.

## Preface
T HR EL 11001 TI
SCADA Standard I/O Schedule
Version 2.0
Issue date: 25 February 2020
Preface
The Asset Standards Authority (ASA) is a key strategic branch of Transport for NSW (TfNSW). As the network design and standards authority for NSW Transport Assets, as specified in the ASA Charter, the ASA identifies, selects, develops, publishes, maintains and controls a suite of requirements documents on behalf of TfNSW, the asset owner. The ASA deploys TfNSW requirements for asset and safety assurance by creating and managing TfNSW's governance models, documents and processes. To achieve this, the ASA focuses on four primary tasks: • publishing and managing TfNSW's process and requirements documents including TfNSW plans, standards, manuals and guides • deploying TfNSW's Authorised Engineering Organisation (AEO) framework • continuously improving TfNSW’s Asset Management Framework • collaborating with the Transport cluster and industry through open engagement The AEO framework authorises engineering organisations to supply and provide asset related products and services to TfNSW. It works to assure the safety, quality and fitness for purpose of those products and services over the asset's whole-of-life. AEOs are expected to demonstrate how they have applied the requirements of ASA documents, including TfNSW plans, standards and guides, when delivering assets and related services for TfNSW. Compliance with ASA requirements by itself is not sufficient to ensure satisfactory outcomes for NSW Transport Assets. The ASA expects that professional judgement be used by competent personnel when using ASA requirements to produce those outcomes. About this document This document is a sample supervisory control and data acquisition (SCADA) I/O schedule that provides information on typical input and output requirements for an electrical SCADA system remote terminal unit (RTU). This document is to be used in conjunction with T HR EL 11001 PR Design Technical Reviews for Electrical SCADA Equipment. This document was originally issued as T HR EL 11001 F1 SCADA Sample I/O Schedule, and two versions were issued. This document was then renumbered, retitled and issued as T HR EL 11001 TI SCADA Standard I/O Schedule, version 1.0. This issue is version 2.0. The changes from T HR EL 11001 TI version 1.0 include updates to reflect new equipment requirements and the modification of some existing equipment requirements.

## Instructions
Instruction notes
1 | This spreadsheet is the I/O Schedule referred to in Section 5.4.2 of T HR EL 11001 PR Design Technical Reviews for Electrical SCADA Equipment. | Abbreviations
2 | Consult the protection concept to determine particular protection indication requirements. | ac | Alternating current
3 | Indications from one relay should not come via the I/O of another relay. | ACCB | ac circuit breaker
4 | Only one pair of Bus Tie CBs should have cable diff trip indications. | AI | Analogue input
5 | Rectifier ACCBs usually have a P127 (OC) relay and a P124 (Backup OC) relay. | BSP | Bulk supply point
6 | New Tx's usually have a P127 (OC) relay and above 1 MVA also have a P632 (differential) relay. | CB | Circuit breaker
7 | New 11 kV and 33 kV feeders usually have P521 (PW) and P127 (OC) relays. | CT | Current transformer
8 | The presence of a fault indicator will need an indication and a remote reset. | dc | Direct current
9 | DNP Index = master station slot x 256 + master station channel (note: this is modified for Invensys RTUs to match 32 channel I/O cards). | DCCB | dc circuit breaker
10 | The RTU channel number starts at '1' whereas the master station channel start at zero. | DI | Digital input
11 | The 'Signal Type' PO changes to DO in the terminal numbering. | DO | Digital output
12 | The master station does not have a rack number. Therefore the master station slot number = (RTU rack number - 1) x 12 + RTU slot. | DNP | Distributed network protocol
13 | Rack, slot, channel are used to calculate the terminal number. | IGIS | Intelligent gas information system
14 | Fail-safe (normally closed contact) is the TfNSW preference for alarm indications. | ILIS | Intelligent light information system
15 | An inverted (non fail-safe) input means the external contact is normally open and closes when the external device state becomes abnormal. | I/O | Input / output
16 | Virtual indications are either RTU software variables or indications received through serial/ethernet links. | MTA | An automatically reset relay with a hand reset flag. It can trip multiple ACCBs.
17 | VTs are normally 33 kV / 110 V (37.5 k V / 125 V) or 11 kV / 110 V (12.5 kV / 125 V), CTs normally have 1 A secondary windings. | MTM | A manually reset relay with a hand reset flag. It can trip multiple ACCBs.
18 | Voltage transducers are normally 125 V / 20 mA, Current transducers are normally 1 A / 20 mA. | OC | Over current protection
19 | The transducer type and model number need to be included in the I/O list. | PLC | Programmable logic controller
20 | The ac feeder rating or the DCCB overcurrent setting needs to be included in the analogue current comments. | PO | Pulse output
21 | It is best to allocate RTU channels to functions in the same order as the functions appear in the cable schedule. | RTU | Remote terminal unit
22 | The Modbus hex addressing is Bus1 will be 1x, Bus2 will be 2x and so on. | TC | Tap changer
23 | Virtual indications from one device should be placed in a group of 16 (one slot) on their own so that if comms are failed the master station slot fails as well. | Tx | Transformer
24 | I/O should be separated by battery system, including I/O cards so that supplies are kept separate. | VT | Voltage transformer
25 | Diagram EL0476613 shows ladder logic for the rectifier control PLC.
26 | Terminals on RTU terminal rail are arranged to suit the RTU hardware modules. Another two terminals are for 125 V negative.
27 | Terminals on field terminal rail are arranged to suit the field cables.

## IO Schedule
| Equipment type | Designation (Desig) | From (Field Equipment Name) | Battery | Cable No | Core No | Field Device Term. | Signal Type | Yellow Fill = Conditional I/O | Signal Status |  |  | CT or VT Ratio | RTU |  |  |  | Master Station | [7 empty] | Hard wired | Comment
Voltage / Network | [8 empty] | Signal Description |  |  |  |  | Rack | Slot | Chan | Terminal | Parameter | DNP Index | I/O Type | Slot | Chan | Invert | Alarm / Log | Delay (s)
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1000 | 1 | X15:01 |  | Control +ve | [7 empty] | R1S10DO/CH2-a | [6 empty] | - |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1000 | 2 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 10 | 4 | R1S10DO/CH2-b | Close | 2561 | PO | 10 | 1 |  | - |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1000 | 3 | X15:02 |  | Control +ve | [7 empty] | R1S10DO/CH1-a | [6 empty] | - |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1000 | 4 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 10 | 3 | R1S10DO/CH1-b | Open | 2560 | PO | 10 | 0 |  | - |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1001 | 1 | X15:08 | DI | ACCB Open | Energised | = | CB Open |  | 1 | 5 | 1 | R1S5DI/1 | Status(1) | 1280 | DI | 5 | 0 |  | A |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1001 | 2 | X15:09 | DI | ACCB Closed | Energised | = | CB Closed |  | 1 | 5 | 2 | R1S5DI/2 | Status(0) | 1281 | DI | 5 | 1 |  | A |  | Y
33kV | Switch | 7XX ISOL | 33kV Feeder Panel | 1 | S1001 | 3 | X15:10 | DI | Disconnector Open | Energised | = | Disc Open |  | 1 | 5 | 3 | R1S5DI/3 | Status(1) | 1282 | DI | 5 | 2 |  | A |  | Y
33kV | Switch | 7XX ISOL | 33kV Feeder Panel | 1 | S1001 | 4 | X15:11 | DI | Disconnector Closed | Energised | = | Disc Closed |  | 1 | 5 | 4 | R1S5DI/4 | Status(0) | 1283 | DI | 5 | 3 |  | A |  | Y
33kV | Switch | 7XX EARTH | 33kV Feeder Panel | 1 | S1001 | 5 | X15:12 | DI | Earth Switch Open | Energised | = | ES Open |  | 1 | 5 | 5 | R1S5DI/5 | Status(1) | 1284 | DI | 5 | 4 |  | A |  | Y
33kV | Switch | 7XX EARTH | 33kV Feeder Panel | 1 | S1001 | 6 | X15:13 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 1 | 5 | 6 | R1S5DI/6 | Status(0) | 1285 | DI | 5 | 5 |  | A |  | Y
66kV | Switch | 8XX Feeder earth | 66kV Feeder Panel | 1 | S1009 | 1 |  | DI | Feeder earth switch open | Energised | = | ES Open |  | 1 | 5 | 11 | R1S5DI/11 | Status(1) | 1290 | DI | 5 | 10 |  | A |  | Y | New 66kV switchgear
66kV | Switch | 8XX Feeder earth | 66kV Feeder Panel | 2 | S1009 | 2 |  | DI | Feeder earth switch closed | Energised | = | ES Closed |  | 1 | 5 | 12 | R1S5DI/12 | Status(0) | 1291 | DI | 5 | 11 |  | A |  | Y | New 66kV switchgear
66kV | Switch | 8XX Fdr Disconnector | 66kV Feeder Panel | 3 | S1009 | 3 |  | DI | Feeder disconnector open | Energised | = | Disc Open |  | 1 | 5 | 13 | R1S5DI/13 | Status(1) | 1292 | DI | 5 | 12 |  | A |  | Y | New 66kV switchgear (Isol 2)
66kV | Switch | 8XX Fdr Disconnector | 66kV Feeder Panel | 4 | S1009 | 4 |  | DI | Feeder disconnector closed | Energised | = | Disc Closed |  | 1 | 5 | 14 | R1S5DI/14 | Status(0) | 1293 | DI | 5 | 13 |  | A |  | Y | New 66kV switchgear (Isol 2)
66kV | Switch | 8XX Fdr Disconnector Earth | 66kV Feeder Panel | 5 | S1009 | 5 |  | DI | Feeder disconnector earth open | Energised | = | ES Open |  | 1 | 5 | 15 | R1S5DI/15 | Status(1) | 1294 | DI | 5 | 14 |  | A |  | Y | New 66kV switchgear (Earth 2)
66kV | Switch | 8XX Fdr Disconnector Earth | 66kV Feeder Panel | 6 | S1009 | 6 |  | DI | Feeder disconnector earth closed | Energised | = | ES Closed |  | 1 | 5 | 16 | R1S5DI/16 | Status(0) | 1295 | DI | 5 | 15 |  | A |  | Y | New 66kV switchgear (Earth 2)
66kV | Switch | 8XX Bus Disconnector | 66kV Feeder Panel | 7 | S1009 | 7 |  | DI | Bus disconnector open | Energised | = | Disc Open |  | 1 | 5 | 17 | R1S5DI/17 | Status(1) | 1296 | DI | 5 | 16 |  | A |  | Y | New 66kV switchgear (Isol 1)
66kV | Switch | 8XX Bus Disconnector | 66kV Feeder Panel | 8 | S1009 | 8 |  | DI | Bus disconnector closed | Energised | = | Disc Closed |  | 1 | 5 | 18 | R1S5DI/18 | Status(0) | 1297 | DI | 5 | 17 |  | A |  | Y | New 66kV switchgear (Isol 1)
66kV | Switch | 8XX Bus Disconnector Earth | 66kV Feeder Panel | 9 | S1009 | 9 |  | DI | Bus disconnector earth open | Energised | = | ES Open |  | 1 | 5 | 19 | R1S5DI/19 | Status(1) | 1298 | DI | 5 | 18 |  | A |  | Y | New 66kV switchgear (Earth 1)
66kV | Switch | 8XX Bus Disconnector Earth | 66kV Feeder Panel | 10 | S1009 | 10 |  | DI | Bus disconnector earth closed | Energised | = | ES Closed |  | 1 | 5 | 20 | R1S5DI/20 | Status(0) | 1299 | DI | 5 | 19 |  | A |  | Y | New 66kV switchgear (Earth 1)
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1001 | 8 | X15:15 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 1 | 5 | 8 | R1S5DI/8 | SpringCharged | 1287 | DI | 5 | 7 |  | A | 10 | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1001 | 9 | X15:16 | DI | ILIS Trip | Energised | = | Trip |  | 1 | 5 | 9 | R1S5DI/9 | ILISTrip | 1288 | DI | 5 | 8 | Y | A |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1001 | 10 | X15:17 | DI | ILIS Fault | Energised | = | Healthy |  | 1 | 5 | 10 | R1S5DI/10 | ILISFault | 1289 | DI | 5 | 9 |  | A |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel |  | IA001 | W | X3:1 | AI | B Phase AC Current +ve | 0-20 mA | = | 0 – 500 A | 500/1A | 1 | 5 | 33 | R1S5AI/CH33+ | Current | 1312 | AI | 5 | 32 |  | A | 10 | Y | Transducer is 1A/10mA
33kV | ACCB | 7XX | 33kV Feeder Panel |  | IA001 | B | X3:4 |  | B Phase AC Current -ve |  |  |  |  | 1 | 5 | 33 | R1S5AI/CH33- | [6 empty] | - |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel |  | IA001 | S |  |  | Screen | [14 empty] | - |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | CM957 | PR1 | X15:32,33 | PULSED | EDMI Mk6E kWh Meter (p10, output 1) | Energised | = | Pulse |  | 1 | 5 | 10 | R1S5DI/10 | Energy | 1290 | DI | 5 | 10 |  | L |  | Y | Bulk supply feeders only.
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | IA160 |  |  | AI | Power Factor | 0-10mA | = | 0-1 | 1/10mA | 1 | 5 | 34 |  | PowerFactor | 1313 | AI | 5 | 33 |  | A | 10 | Y | Bulk supply feeders only.
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1002 | 2 | X15:30 | DI | VT MCB Closed (Directional Protection Voltage Fail) | Energised | = | MCB Closed |  | 1 | 5 | 12 | R1S5DI/12 | DirProtVoltage | 1291 | DI | 5 | 11 |  | A |  | Y | Supplied from Q1
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1004 | 1 |  | DI | Low Gas (Stage 1) | Energised | = | Gas Level OK |  | 1 | 5 | 9 | R1S5DI/9 | Low Gas | 1294 | DI | 5 | 14 |  | A |  | Y | Switchgear dependent
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1004 | 2 |  | DI | Low Gas Lockout (Stage 2) | Energised | = | Locked out |  | 1 | 5 | 10 | R1S5DI/10 | Low Gas L/O | 1295 | DI | 5 | 15 | Y | A |  | Y | Switchgear dependent
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1004 | 3 |  | DI | Motor Trouble | Energised | = | Motor Healthy |  | 1 | 5 | 11 | R1S5DI/11 | Motor Trouble | 1296 | DI | 5 | 16 |  | A |  | Y | Switchgear dependent
33kV | ACCB | 7XX | 33kV Feeder Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | PWRelayCommsFail | 37120 | DI | 145 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1002 | 1 | X15:24 | DI | PW Relay (P521) Watchdog | Energised | = | Relay Healthy |  | 1 | 5 | 18 | R1S5DI/18 | PWRelayFail | 1297 | DI | 5 | 17 |  | A |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1002 | 3 |  | DI | Pilot Wire Trip (mhobo4) | Energised | = | Fault on feeder |  | 1 | 5 | 19 | R1S5DI/19 | PilotWireTrip | 1298 | DI | 5 | 18 | Y | A |  | Y | Not required, except for older relays.
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 0 | P521 | Serial | Pilot Wire Trip Alarm (A-Phase) | High | = | PW Fault | [5 empty] | PWTripA | 37121 | DI | 145 | 1 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 1 | P521 | Serial | Pilot Wire Trip Alarm (B-Phase) | High | = | PW Fault | [5 empty] | PWTripB | 37122 | DI | 145 | 2 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 2 | P521 | Serial | Pilot Wire Trip Alarm (C-Phase) | High | = | PW Fault | [5 empty] | PWTripC | 37123 | DI | 145 | 3 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 3 | P521 | Serial | Pilot Wire Trip Alarm (AB-Phase) | High | = | PW Fault | [5 empty] | PWTripAB | 37124 | DI | 145 | 4 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 4 | P521 | Serial | Pilot Wire Trip Alarm (AC-Phase) | High | = | PW Fault | [5 empty] | PWTripAC | 37125 | DI | 145 | 5 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 5 | P521 | Serial | Pilot Wire Trip Alarm (BC-Phase) | High | = | PW Fault | [5 empty] | PWTripBC | 37126 | DI | 145 | 6 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 6 | P521 | Serial | Pilot Wire Trip Alarm (ABC-Phase) | High | = | PW Fault | [5 empty] | PWTripABC | 37127 | DI | 145 | 7 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 7 | P521 | Serial | Trip Circuit 1 Supervision Alarm | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 37128 | DI | 145 | 8 |  | A |  |  | Hardwired if from dedicated TC relay
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 8 | P521 | Serial | CB Fail Alarm (TC1 – P521) | High | = | CB did not trip – TC1 | [5 empty] | BreakerFailPW | 37129 | DI | 145 | 9 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 2 | BIT 9 | P521 | Serial | Pilot Communications Failed | High | = | Comms Failed | [5 empty] | PilotWireFail | 37130 | DI | 145 | 10 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | OverCurrRelayCommFail | 36864 | DI | 144 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1002 | 4 | X15:26 | DI | DOC & DEF Relay (P127/P14D) Watchdog | Energised | = | Relay Healthy |  | 1 | 5 | 20 | R1S5DI/20 | OverCurrentRelay | 1299 | DI | 5 | 19 |  | A |  | Y
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1002 | 5 | X15:28 | DI | DOC Trip | Energised | = | O/C Fault |  | 1 | 5 | 21 | R1S5DI/21 | OverCurrent | 1300 | DI | 5 | 20 | Y | A |  | Y | Not required, except for older relays.
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 0 | P127/14D | Serial | DOC Trip Alarm (A-phase) | High | = | O/C Fault | [5 empty] | OverCurrentA | 36865 | DI | 144 | 1 | Y | A |  |  | These relays can perform
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 1 | P127/14D | Serial | DOC Trip Alarm (B-phase) | High | = | O/C Fault | [5 empty] | OverCurrentB | 36866 | DI | 144 | 2 | Y | A |  |  | OverCurrent\DirOverCurr\InstOverCurr
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 2 | P127/14D | Serial | DOC Trip Alarm (C-phase) | High | = | O/C Fault | [5 empty] | OverCurrentC | 36867 | DI | 144 | 3 | Y | A |  |  | or a combination of the above
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 3 | P127/14D | Serial | DOC Trip Alarm (AB-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAB | 36868 | DI | 144 | 4 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 4 | P127/14D | Serial | DOC Trip Alarm (AC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAC | 36869 | DI | 144 | 5 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 5 | P127/14D | Serial | DOC Trip Alarm (BC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentBC | 36870 | DI | 144 | 6 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 6 | P127/14D | Serial | DOC Trip Alarm (ABC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentABC | 36871 | DI | 144 | 7 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 7 | P127/14D | Serial | DEF Trip Alarm | High | = | Earth Fault | [5 empty] | OverCurEarthLeakTrip | 36872 | DI | 144 | 8 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 1 | BIT 8 | P127/14D | Serial | Trip Circuit 2 Supervision Alarm | Low | = | TC2 Healthy | [5 empty] | TripCircuitSupervision2 | 36873 | DI | 144 | 9 |  | A |  |  | Hardwired if from dedicated TC relay
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 9 | P127/14D | Serial | CB Fail Alarm (TC2 – P127/P14D) | High | = | CB did not trip – TC2 | [5 empty] | BreakerFailOC | 36874 | DI | 144 | 10 | Y | A
33kV | ACCB | 7XX | 33kV Feeder Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | PWRelayCommsFail | 37120 | DI | 145 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1003 | 1 | X15:29 | DI | PW Relay (P543) Watchdog | Energised | = | Relay Healthy |  | 1 | 5 | 18 | R1S5DI/18 | PWRelayFail | 1297 | DI | 5 | 17 |  | A |  | Y | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 0 | P543 | Serial | Pilot Wire Trip Alarm (A-Phase) | High | = | PW Fault | [5 empty] | PWTripA | 37121 | DI | 145 | 1 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 1 | P543 | Serial | Pilot Wire Trip Alarm (B-Phase) | High | = | PW Fault | [5 empty] | PWTripB | 37122 | DI | 145 | 2 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 2 | P543 | Serial | Pilot Wire Trip Alarm (C-Phase) | High | = | PW Fault | [5 empty] | PWTripC | 37123 | DI | 145 | 3 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 3 | P543 | Serial | Pilot Wire Trip Alarm (AB-Phase) | High | = | PW Fault | [5 empty] | PWTripAB | 37124 | DI | 145 | 4 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 4 | P543 | Serial | Pilot Wire Trip Alarm (AC-Phase) | High | = | PW Fault | [5 empty] | PWTripAC | 37125 | DI | 145 | 5 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 5 | P543 | Serial | Pilot Wire Trip Alarm (BC-Phase) | High | = | PW Fault | [5 empty] | PWTripBC | 37126 | DI | 145 | 6 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 6 | P543 | Serial | Pilot Wire Trip Alarm (ABC-Phase) | High | = | PW Fault | [5 empty] | PWTripABC | 37127 | DI | 145 | 7 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 7 | P543 | Serial | Trip Circuit 1 Supervision Alarm | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 37128 | DI | 145 | 8 |  | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 8 | P543 | Serial | CB Fail Alarm (TC1 – P543) | High | = | CB did not trip – TC1 | [5 empty] | BreakerFailPW | 37129 | DI | 145 | 9 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel |  | Word 3 | BIT 9 | P543 | Serial | Pilot Communications Failed | High | = | Comms Failed | [5 empty] | PilotWireFail | 37130 | DI | 145 | 10 | Y | A |  |  | Differential relay for bulk supply points
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1005 | 1 | Intertrip relay | DI | Aux Supply Failed (mrtp03) | Energised | = | Failed |  | 1 | 5 | 22 |  | InterTripRelayFail | 1301 | DI | 5 | 21 |  | A |  | Y | Only required for bulk supply points. From relay in pilot wire protection panel
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1005 | 2 | Intertrip relay | DI | PW Intertrip Relay Failed | Energised | = | Failed |  | 1 | 5 | 23 |  | InterTripRelayFail | 1302 | DI | 5 | 22 |  | A |  | Y | Only required for bulk supply points. From relay in pilot wire protection panel
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1005 | 3 | Intertrip relay | DI | Intertrip Received (srr) | Energised | = | Received |  | 1 | 5 | 24 |  | InterTripReceive | 1303 | DI | 5 | 23 | Y | A |  | Y | Only required for bulk supply points. From relay in pilot wire protection panel
33kV | ACCB | 7XX | 33kV Feeder Panel | 1 | S1005 | 4 | Intertrip relay | DI | Intertrip Send | Energised | = | Sent |  | 1 | 5 | 25 |  | InterTripSend | 1304 | DI | 5 | 24 | Y | A |  | Y | Only required for bulk supply points. From relay in pilot wire protection panel
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1006 | 1 | X15:1 |  | Control +ve | [7 empty] | R1S10DO/CH4-a | [6 empty] | - |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1006 | 2 | X15:3 | PO | Remote Close Command |  |  |  |  | 1 | 10 | 4 | R1S10DO/CH4-b | Close | 2563 | PO | 10 | 3 |  | - |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1006 | 3 | X15:2 |  | Control +ve | [7 empty] | R1S10DO/CH3-a | [6 empty] | - |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1006 | 4 | X15:4 | PO | Remote Open Command |  |  |  |  | 1 | 10 | 3 | R1S10DO/CH3-b | Open | 2562 | PO | 10 | 2 |  | - |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1007 | 1 | X15:8 | DI | ACCB Open | Energised | = | CB Open |  | 1 | 5 | 26 | R1S5DI/26 | Status(1) | 1305 | DI | 5 | 25 |  | A |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1007 | 2 | X15:9 | DI | ACCB Closed | Energised | = | CB Closed |  | 1 | 5 | 27 | R1S5DI/27 | Status(0) | 1306 | DI | 5 | 26 |  | A |  | Y
33kV | Switch | 33KV 1-2 BS ISOL | 33kV Bus Section Panel | 1 | S1007 | 3 | X15:10 | DI | Disconnector Open | Energised | = | DISC Open |  | 1 | 5 | 28 | R1S5DI/28 | Status(1) | 1307 | DI | 5 | 27 |  | A |  | Y
33kV | Switch | 33KV 1-2 BS ISOL | 33kV Bus Section Panel | 1 | S1007 | 4 | X15:11 | DI | Disconnector Closed | Energised | = | DISC Closed |  | 1 | 5 | 29 | R1S5DI/29 | Status(0) | 1308 | DI | 5 | 28 |  | A |  | Y
33kV | Switch | 33KV 1-2 BS EARTH | 33kV Bus Section Panel | 1 | S1007 | 5 | X15:12 | DI | Earth Switch Open | Energised | = | ES Open |  | 1 | 5 | 30 | R1S5DI/30 | Status(1) | 1309 | DI | 5 | 29 |  | A |  | Y
33kV | Switch | 33KV 1-2 BS EARTH | 33kV Bus Section Panel | 1 | S1007 | 6 | X15:14 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 1 | 5 | 31 | R1S5DI/31 | Status(0) | 1310 | DI | 5 | 30 |  | A |  | Y
66kV | Switch | 66KV 1-2 BS BS1 FES | 66kV Bus Section Panel | 1 | S1009 | 1 |  | DI | BS1 FES open | Energised | = | ES Open |  | 1 | 5 | 11 | R1S5DI/11 | Status(1) | 1290 | DI | 5 | 10 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS1 FES | 66kV Bus Section Panel | 1 | S1009 | 2 |  | DI | BS1 FES closed | Energised | = | ES Closed |  | 1 | 5 | 12 | R1S5DI/12 | Status(0) | 1291 | DI | 5 | 11 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS1 Disconnector | 66kV Bus Section Panel | 1 | S1009 | 3 |  | DI | BS1 disconnector open | Energised | = | Disc Open |  | 1 | 5 | 13 | R1S5DI/13 | Status(1) | 1292 | DI | 5 | 12 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS1 Disconnector | 66kV Bus Section Panel | 1 | S1009 | 4 |  | DI | BS1 disconnector closed | Energised | = | Disc Closed |  | 1 | 5 | 14 | R1S5DI/14 | Status(0) | 1293 | DI | 5 | 13 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS1 Disconnector Earth | 66kV Bus Section Panel | 1 | S1009 | 5 |  | DI | BS1 disconnector earth open | Energised | = | ES Open |  | 1 | 5 | 15 | R1S5DI/15 | Status(1) | 1294 | DI | 5 | 14 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS1 Disconnector Earth | 66kV Bus Section Panel | 1 | S1009 | 6 |  | DI | BS1 disconnector earth closed | Energised | = | ES Closed |  | 1 | 5 | 16 | R1S5DI/16 | Status(0) | 1295 | DI | 5 | 15 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS2 Disconnector | 66kV Bus Section Panel | 1 | S1009 | 7 |  | DI | BS2 disconnector open | Energised | = | Disc Open |  | 1 | 5 | 17 | R1S5DI/17 | Status(1) | 1296 | DI | 5 | 16 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS2 Disconnector | 66kV Bus Section Panel | 1 | S1009 | 8 |  | DI | BS2 disconnector closed | Energised | = | Disc Closed |  | 1 | 5 | 18 | R1S5DI/18 | Status(0) | 1297 | DI | 5 | 17 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS2 Disconnector Earth | 66kV Bus Section Panel | 1 | S1009 | 9 |  | DI | BS2 disconnector earth open | Energised | = | ES Open |  | 1 | 5 | 19 | R1S5DI/19 | Status(1) | 1298 | DI | 5 | 18 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS2 Disconnector Earth | 66kV Bus Section Panel | 1 | S1009 | 10 |  | DI | BS2 disconnector earth closed | Energised | = | ES Closed |  | 1 | 5 | 20 | R1S5DI/20 | Status(0) | 1299 | DI | 5 | 19 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS2 FES | 66kV Bus Section Panel | 1 | S1009 | 11 |  | DI | BS2 FES open | Energised | = | ES Open |  | 1 | 5 | 21 | R1S5DI/21 | Status(1) | 1300 | DI | 5 | 20 |  | A |  | Y | Indoor 66kV GIS Switchgear
66kV | Switch | 66KV 1-2 BS BS2 FES | 66kV Bus Section Panel | 1 | S1009 | 12 |  | DI | BS2 FES closed | Energised | = | ES Closed |  | 1 | 5 | 22 | R1S5DI/22 | Status(0) | 1301 | DI | 5 | 21 |  | A |  | Y | Indoor 66kV GIS Switchgear
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1007 | 7 | X15:16 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 1 | 5 | 32 | R1S5DI/32 | SpringCharged | 1311 | DI | 5 | 31 |  | A | 10 | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1020 | 1 |  | DI | Low Gas (Stage 1) | Energised | = | Gas Level OK |  | 1 | 6 | 3 | R1S6DI/3 | Low Gas | 1538 | DI | 6 | 2 |  | A |  | Y | Switchgear dependent
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1020 | 2 |  | DI | Low Gas Lockout (Stage 2) | Energised | = | Locked out |  | 1 | 6 | 4 | R1S6DI/4 | Low Gas L/O | 1539 | DI | 6 | 3 | Y | A |  | Y | Switchgear dependent
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1020 | 3 |  | DI | Motor Trouble | Energised | = | Motor Healthy |  | 1 | 6 | 5 | R1S6DI/5 | Motor Trouble | 1540 | DI | 6 | 4 |  | A |  | Y | For outdoor SF6 switchgear. Switchgear dependent
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 9 | X15:19 | DI | BZ ILIS Trip | Energised | = | Trip |  | 1 | 6 | 7 | R1S6DI/7 | ILISTrip | 1542 | DI | 6 | 6 | Y | A |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 10 | X15:20 | DI | BZ ILIS Fault | Energised | = | Healthy |  | 1 | 6 | 8 | R1S6DI/8 | ILISFault | 1543 | DI | 6 | 7 |  | A |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 11 | X15:21 | DI | Trip Circuit 1 Supervision Alarm | Energised | = | TC 1 Healthy |  | 1 | 6 | 9 | R1S6DI/9 | TripCircuitSupervision1 | 4117 | DI | 16 | 21 |  | A |  | Y | From TC relay 1TM10
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 12 | X15:22 | DI | Trip Circuit 2 Supervision Alarm | Energised | = | TC 2 Healthy |  | 1 | 6 | 10 | R1S6DI/10 | TripCircuitSupervision2 | 4118 | DI | 16 | 22 |  | A |  | Y | From TC relay 1TM10
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 11 |  | DI | Cable Diff Trip Alarm (A-Phase) | Energised | = | Diff Fault |  | 1 | 6 | 11 | R1S6DI/11 | DifferentialTripA | 1544 | DI | 6 | 8 | Y | A |  | Y | Diff is usually MCAG34 relay + P127 for BSPs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 12 |  | DI | Cable Diff Trip Alarm (B-Phase) | Energised | = | Diff Fault |  | 1 | 6 | 12 | R1S6DI/12 | DifferentialTripB | 1545 | DI | 6 | 9 | Y | A |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 13 |  | DI | Cable Diff Trip Alarm (C-Phase) | Energised | = | Diff Fault |  | 1 | 6 | 13 | R1S6DI/13 | DifferentialTripC | 1546 | DI | 6 | 10 | Y | A |  | Y
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1008 | 14 | X15:24 | DI | Cable Diff Relay (P127) Watchdog | Energised | = | Relay Healthy |  | 1 | 6 | 14 | R1S6DI/14 | DiffRelayFail | 1547 | DI | 6 | 11 |  | A |  | Y | Required for Bus Tie CBs at bulk supplies
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | DiffRelayCommFail | 32768 | DI | 128 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 4 | BIT 0 | P127 | Serial | Cable Diff Trip Alarm | High | = | Diff Fault | [5 empty] | DifferentialTrip | 32769 | DI | 128 | 1 | Y | A |  |  | For BSPs only
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 4 | BIT 1 | P127 | Serial | Trip Circuit 1 Supervision Alarm (TC2) | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 32770 | DI | 128 | 2 |  | A |  |  | Hardwired if from dedicated TC relay
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 4 | BIT 2 | P127 | Serial | CB Fail Alarm (TC1 - P127) | High | = | CB did not trip | [5 empty] | DiffBreakerFail | 32771 | DI | 128 | 3 | Y | A |  |  | For BSPs only
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 4 | BIT 3 | P127 | Serial | Cable Diff Trip Alarm (A-Phase) | High | = | Diff Fault | [5 empty] | DifferentialTripA | 32772 | DI | 128 | 4 | Y | A |  |  | For BSPs only
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 4 | BIT 4 | P127 | Serial | Cable Diff Trip Alarm (B-Phase) | High | = | Diff Fault | [5 empty] | DifferentialTripB | 32773 | DI | 128 | 5 | Y | A |  |  | For BSPs only
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 4 | BIT 5 | P127 | Serial | Cable Diff Trip Alarm (C-Phase) | High | = | Diff Fault | [5 empty] | DifferentialTripC | 32774 | DI | 128 | 6 | Y | A |  |  | For BSPs only
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | 1 | S1020 | 1 | P124/7,P14D/N | DI | Over Current Relay | Low | = | Relay Healthy |  | 1 | 6 | 15 | R1S6DI/15 | OverCurrentRelay | 1548 | DI | 6 | 12 |  | A |  | Y | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | OverCurrRelayCommFail | 33024 | DI | 129 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 0 | P124/7,P14D/N | Serial | OC Trip Alarm (A-phase) | High | = | O/C Fault | [5 empty] | OverCurrentA | 33025 | DI | 129 | 1 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 1 | P124/7,P14D/N | Serial | OC Trip Alarm (B-phase) | High | = | O/C Fault | [5 empty] | OverCurrentB | 33026 | DI | 129 | 2 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 2 | P124/7,P14D/N | Serial | OC Trip Alarm (C-phase) | High | = | O/C Fault | [5 empty] | OverCurrentC | 33027 | DI | 129 | 3 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 3 | P124/7,P14D/N | Serial | OC Trip Alarm (AB-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAB | 33028 | DI | 129 | 4 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 4 | P124/7,P14D/N | Serial | OC Trip Alarm (AC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAC | 33029 | DI | 129 | 5 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 5 | P124/7,P14D/N | Serial | OC Trip Alarm (BC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentBC | 33030 | DI | 129 | 6 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 6 | P124/7,P14D/N | Serial | OC Trip Alarm (ABC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentABC | 33031 | DI | 129 | 7 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 7 | P124/7,P14D/N | Serial | Trip Circuit 2 Supervision Alarm (TC2) | Low | = | TC2 Healthy | [5 empty] | TripCircuitSupervision2 | 33032 | DI | 129 | 8 |  | A |  |  | Hardwired if from dedicated TC relay
33kV | ACCB | 33KV 1-2 BS | 33kV Bus Section Panel |  | Word 5 | BIT 8 | P124/7,P14D/N | Serial | CB Fail Alarm (TC2) | High | = | CB did not trip | [5 empty] | BreakerFailOC | 33033 | DI | 129 | 9 | Y | A |  |  | OC relay may exist for outdoor CBs
33kV | ACCB | 33KV BS1 | Bus Section Panel | 1 | S1019 | 3 | X15:28 | DI | IGIS PRE-Warning Alarm – BUS 1 (P200) | Energised | = | Healthy |  | 1 | 6 | 11 | R1S6DI/11 | IGIS Alarm | 1546 | DI | 6 | 10 |  | A |  | Y | From either Bus Section or Feeder ACCB
33kV | ACCB | 33KV BS1 | Bus Section Panel | 1 | S1019 | 4 | X15:30 | DI | IGIS Warning Alarm – BUS 1 (P200) | Energised | = | Healthy |  | 1 | 6 | 12 | R1S6DI/12 | IGIS Warning | 1547 | DI | 6 | 11 |  | A |  | Y | From either Bus Section or Feeder ACCB
33kV | ACCB | 33KV BS1 | Bus Section Panel | 1 | S1019 | 5 | X15:33 | DI | IGIS Fault – BUS 1 (P200) | Energised | = | Fault |  | 1 | 6 | 13 | R1S6DI/13 | IGIS Fault | 1548 | DI | 6 | 12 | Y | A |  | Y | From either Bus Section or Feeder ACCB
33kV | ACCB | 33KV 1-2 BS | Bus Section Panel | 1 | S1019 | 10 | X15:27 | DI | Busbar Protection Supply (k10) | Energised | = | Supply Healthy |  | 1 | 6 | 14 | R1S6DI/14 | BZ Supply | 1549 | DI | 6 | 13 |  | A |  | Y | From either Bus Section or Feeder ACCB
33kV | ACCB | 33KV 1-2 BS | Bus Section Panel | 1 | S1019 | 1 | X15:26 | DI | Busbar Protection MTM Trip (k86b) | Energised | = | Fault |  | 1 | 6 | 15 | R1S6DI/15 | BZ Lockout | 1550 | DI | 6 | 14 | Y | A |  | Y | From either Bus Section or Feeder ACCB
33kV | ACCB | 33KV 1-2 BS | Bus Section Panel | 1 | S4017 | 20 |  | DI | Cable Differential Protection MTM Trip | Energised | = | CB locked out |  | 1 | 6 | 16 | R1S6DI/16 | Lockout | 1551 | DI | 6 | 15 | Y | A |  | Y | From either Bus Section or Feeder ACCB
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1010 | 1 | X15:1 |  | Control +ve | [7 empty] | R1S10DO/CH6-a | [6 empty] | - |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1010 | 2 | X15:23 | PO | Remote Close Command |  |  |  |  | 1 | 10 | 6 | R1S10DO/CH6-b | Close | 2565 | PO | 10 | 5 |  | - |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1010 | 3 | X15:2 |  | Control +ve | [7 empty] | R1S10DO/CH5-a | [6 empty] | - |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1010 | 4 | X15:24 | PO | Remote Open Command |  |  |  |  | 1 | 10 | 5 | R1S10DO/CH5-b | Open | 2564 | PO | 10 | 4 |  | - |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1011 | 1 | X15:56 | DI | ACCB Open | Energised | = | CB Open |  | 1 | 6 | 17 | R1S6DI/17 | Status(1) | 1552 | DI | 6 | 16 |  | A |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1011 | 2 | X15:57 | DI | ACCB Closed | Energised | = | CB Closed |  | 1 | 6 | 18 | R1S6DI/18 | Status(0) | 1553 | DI | 6 | 17 |  | A |  | Y
33kV | Switch | R1 ACCB ISOL | Rectifier ACCB Panel | 1 | S1011 | 3 | X15:58 | DI | Disconnector Open | Energised | = | DISC Open |  | 1 | 6 | 19 | R1S6DI/19 | Status(1) | 1554 | DI | 6 | 18 |  | A |  | Y
33kV | Switch | R1 ACCB ISOL | Rectifier ACCB Panel | 1 | S1011 | 4 | X15:59 | DI | Disconnector Closed | Energised | = | DISC Closed |  | 1 | 6 | 20 | R1S6DI/20 | Status(0) | 1555 | DI | 6 | 19 |  | A |  | Y
33kV | Switch | R1 ACCB EARTH | Rectifier ACCB Panel | 1 | S1011 | 5 | X15:60 | DI | Earth Switch Open | Energised | = | ES Open |  | 1 | 6 | 21 | R1S6DI/21 | Status(1) | 1556 | DI | 6 | 20 |  | A |  | Y
33kV | Switch | R1 ACCB EARTH | Rectifier ACCB Panel | 1 | S1011 | 6 | X15:62 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 1 | 6 | 22 | R1S6DI/22 | Status(0) | 1557 | DI | 6 | 21 |  | A |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1011 | 7 | X15:64 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 1 | 6 | 24 | R1S6DI/24 | SpringCharged | 1559 | DI | 6 | 23 |  | A | 10 | Y | Add delay at Master Station if this comes up while charging
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1011 | 8 | X15:66 | DI | ILIS Trip | Energised | = | Trip |  | 1 | 6 | 27 | R1S6DI/27 | ILISTrip | 1562 | DI | 6 | 26 | Y | A |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1011 | 9 | X15:67 | DI | ILIS Fault | Energised | = | Healthy |  | 1 | 6 | 28 | R1S6DI/28 | ILISFault | 1563 | DI | 6 | 27 |  | A |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | IA030 | W | X3:1 | AI | B Phase AC Current +ve | 0-20 mA | = | 0 – 300A | 300/1A | 1 | 5 | 35 | R1S5AI/CH35 + | Current | 1314 | AI | 5 | 34 |  | A | 10 | Y | Transducer is 1A/20mA
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | IA030 | B | X3:4 |  | B Phase AC Current -ve |  |  |  |  | 1 | 5 | 35 | R1S5AI/CH35 - | [8 empty] | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | IA030 | S |  |  | Screen | [16 empty] | Y
33kV | ACCB | R1 ACCB | [6 empty] | Sum of all Rectifier currents |  |  | 0 - 300A | [5 empty] | ACCurrentSum | 34048 | AI | 133 | 0 |  | A | 10 |  | Internal RTU calculation
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1020 | 1 |  | DI | Low Gas (Stage 1) | Energised | = | Gas Level OK |  | 1 | 6 | 29 | R1S6DI/29 | Low Gas | 1564 | DI | 6 | 28 |  | A |  | Y | Switchgear dependent
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1020 | 2 |  | DI | Low Gas Lockout (Stage 2) | Energised | = | Locked out |  | 1 | 6 | 30 | R1S6DI/30 | Low Gas L/O | 1565 | DI | 6 | 29 | Y | A |  | Y | Switchgear dependent
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1020 | 3 |  | DI | Motor Trouble | Energised | = | Motor Healthy |  | 1 | 6 | 31 | R1S6DI/31 | Motor Trouble | 1566 | DI | 6 | 30 |  | A |  | Y | For outdoor SF6 switchgear. Switchgear dependent
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1015 | 6 | X15:78 | DI | Primary Protection Aux Supply Failed | Energised | = | MCB Closed |  | 1 | 6 | 32 | R1S6DI/32 | Prot Aux Supply | 1567 | DI | 6 | 31 |  | A |  | Y | Required if supplied from AC Aux not if self powered
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1012 | 1 | X15:26 | DI | Primary Protection Relay Watchdog | Energised | = | Relay Healthy |  | 1 | 7 | 1 | R1S7DI/1 | InstOverCurrentRelay | 1792 | DI | 7 | 0 |  | A |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | OverCurrRelayCommFail | 34304 | DI | 134 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 0 | P124/14N | Serial | Primary Prot Trip Alarm (A-Phase) | High | = | Fault | [5 empty] | InstOverCurrentA | 34305 | DI | 134 | 1 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 1 | P124/14N | Serial | Primary Prot Trip Alarm (B-Phase) | High | = | Fault | [5 empty] | InstOverCurrentB | 34306 | DI | 134 | 2 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 2 | P124/14N | Serial | Primary Prot Trip Alarm (C-Phase) | High | = | Fault | [5 empty] | InstOverCurrentC | 34307 | DI | 134 | 3 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 3 | P124/14N | Serial | Primary Prot Trip Alarm (AB-Phase) | High | = | Fault | [5 empty] | InstOverCurrentAB | 34308 | DI | 134 | 4 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 4 | P124/14N | Serial | Primary Prot Trip Alarm (AC-Phase) | High | = | Fault | [5 empty] | InstOverCurrentAC | 34309 | DI | 134 | 5 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 5 | P124/14N | Serial | Primary Prot Trip Alarm (BC-Phase) | High | = | Fault | [5 empty] | InstOverCurrentBC | 34310 | DI | 134 | 6 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 6 | P124/14N | Serial | Primary Prot Trip Alarm (ABC-Phase) | High | = | Fault | [5 empty] | InstOverCurrentABC | 34311 | DI | 134 | 7 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 7 | P124/14N | Serial | Primary Prot Trip Alarm (Earth fault) | High | = | Fault | [5 empty] | InstEarthLeakage | 34312 | DI | 134 | 8 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 8 | P124/14N | Serial | Trip Circuit 1 Supervision Alarm | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 34313 | DI | 134 | 9 |  | A |  |  | Hardwired if from dedicated TC relay
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-5 | BIT 9 | P124/14N | Serial | CB Fail Alarm (TC1 – P124/P14N) | High | = | CB did not trip – TC1 | [5 empty] | BreakerFailOC | 34314 | DI | 134 | 10 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | 1 | S1005 | 2 | X15:26 | DI | Backup Protection Relay Watchdog | Energised | = | Relay Healthy |  | 1 | 7 | 2 | R1S7DI/2 | OverCurrentRelay | 1793 | DI | 7 | 1 |  | A |  | Y
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | OverCurrRelayCommFail | 33280 | DI | 130 | 0 |  | A | 10 |  | Internal to RTU
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 0 | P127 | Serial | Backup Prot Trip Alarm (A-phase) | High | = | Fault | [5 empty] | OverCurrentA | 33281 | DI | 130 | 1 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 1 | P127 | Serial | Backup Prot Trip Alarm (B-phase) | High | = | Fault | [5 empty] | OverCurrentB | 33282 | DI | 130 | 2 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 2 | P127 | Serial | Backup Prot Trip Alarm (C-phase) | High | = | Fault | [5 empty] | OverCurrentC | 33283 | DI | 130 | 3 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 3 | P127 | Serial | Backup Prot Trip Alarm (AB-phase) | High | = | Fault | [5 empty] | OverCurrentAB | 33284 | DI | 130 | 4 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 4 | P127 | Serial | Backup Prot Trip Alarm (AC-phase) | High | = | Fault | [5 empty] | OverCurrentAC | 33285 | DI | 130 | 5 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 5 | P127 | Serial | Backup Prot Trip Alarm (BC-phase) | High | = | Fault | [5 empty] | OverCurrentBC | 33286 | DI | 130 | 6 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 6 | P127 | Serial | Backup Prot Trip Alarm (ABC-phase) | High | = | Fault | [5 empty] | OverCurrentABC | 33287 | DI | 130 | 7 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 7 | P127 | Serial | Backup Prot Trip Alarm (Earth fault) | High | = | Fault | [5 empty] | EarthFault | 33288 | DI | 130 | 8 | Y | A
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 8 | P127 | Serial | Trip Circuit 2 Supervision Alarm | Low | = | TC2 Healthy | [5 empty] | TripCircuitSupervision2 | 33289 | DI | 130 | 9 |  | A |  |  | Hardwired if from dedicated TC relay
33kV | ACCB | R1 ACCB | Rectifier ACCB Panel |  | WORD-6 | BIT 8 | P127 | Serial | CB FAIL Alarm (TC2 – P127) | High | = | CB did not trip – TC2 | [5 empty] | BreakerFail | 33290 | DI | 130 | 10 | Y | A
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA093 | W |  | AI | Rectifier No.1 Top (Exit) Air Temp +ve | 0-20 mA | = | 0 – 80oc |  | 1 | 6 | 33 | R1S6AI/CH33 + | RectTopTemp | 1568 | AI | 6 | 32 |  | A | 10 | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA093 | B |  |  | Rectifier No.1 Top (Exit) Air Temp -ve | [7 empty] | R1S6AI/CH33 - | [8 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA093 | S |  |  | Screen | [16 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA092 | W |  | AI | Rectifier No.1 Bottom (Entry) Air Temp +ve | 0-20 mA | = | 0 – 80oc |  | 1 | 6 | 34 | R1S6AI/CH34 + | RectBottomTemp | 1569 | AI | 6 | 33 |  | A | 10 | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA092 | B |  |  | Rectifier No.1 Bottom (Entry) Air Temp -ve | [7 empty] | R1S6AI/CH34 - | [8 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA092 | S |  |  | Screen | [16 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA091 | W |  | AI | Transformer Winding Temp +ve | 0-20 mA | = | 0 - 150°C |  | 1 | 6 | 35 | R1S6AI/CH35 + | TXHotSpotTemp | 1570 | AI | 6 | 34 |  | A | 10 | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA091 | B |  |  | Transformer Winding Temp -ve | [7 empty] | R1S6AI/CH35 - | [8 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA091 | S |  |  | Screen | [16 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA090 | W |  | AI | Transformer Oil Temp +ve | 0-20 mA | = | 0 - 150°C |  | 1 | 6 | 36 | R1S6AI/CH36 + | TXTopOilTemp | 1571 | AI | 6 | 35 |  | A | 10 | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA090 | B |  |  | Transformer Oil Temp -ve | [7 empty] | R1S6AI/CH36 - | [8 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | IA090 | S |  |  | Screen | [16 empty] | Y
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1015 | 10 |  | DI | Rectifier Tx Frame Leakage (k64fl) | Energised | = | Fault |  | 1 | 7 | 3 | R1S7DI/3 |  | 1794 | DI | 7 | 2 | Y | A |  | Y | Only required where Rect Tx is located within a roofed enclosure
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1034 | 9 |  | DI | Winding Temp Critical Alarm | Energised | = | Passed Critical Temp |  | 1 | 7 | 4 | R1S7DI/4 | TXWdgTempCritical | 1795 | DI | 7 | 3 | Y | A |  | Y
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1034 | 10 |  | DI | Oil Temp Critical Alarm | Energised | = | Passed Critical Temp |  | 1 | 7 | 5 | R1S7DI/5 | TXOilTempCritical | 1796 | DI | 7 | 4 | Y | A |  | Y
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1034 | 12 |  | DI | Winding Temp Alarm | Energised | = | Passed Lower Temp |  | 1 | 7 | 7 | R1S7DI/7 | TXWdgTempAlarm | 1798 | DI | 7 | 6 | Y | A |  | Y
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1034 | 13 |  | DI | Oil Temp Alarm | Energised | = | Passed Lower Temp |  | 1 | 7 | 8 | R1S7DI/8 | TXOilTempAlarm | 1799 | DI | 7 | 7 | Y | A |  | Y
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1034 | 14 |  | DI | Main Tank High Oil | Energised | = | Oil Not High Level |  | 1 | 7 | 9 | R1S7DI/9 | TXMainOilHigh | 1800 | DI | 7 | 8 |  | A |  | Y
1500VDC | Rectifier | R1 TX | Rectifier No. 1 | 1 | S1034 | 15 |  | DI | Main Tank Low Oil | Energised | = | Oil Not Low Level |  | 1 | 7 | 10 | R1S7DI/10 | TXMainOilLow | 1801 | DI | 7 | 9 |  | A |  | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 | [6 empty] | Low | = | Comms Healthy | [5 empty] | PLCCommsFail | 38144 | DI | 149 | 0 |  | A | 10 |  | Internal to RTU
1500VDC | Rectifier | R1 | Rectifier No. 1 | 1 | S1015 | 7 | X15:73 | DI | PLC Fault (K97) | Energised | = | Fault |  | 1 | 7 | 11 | R1S7DI/11 | PLCFault | 1802 | DI | 7 | 10 |  | A |  | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | Modbus 10 | BIT 0 | PLC | Serial | Buchholz Oil Trip | High | = | Buchholz Oil Fault | [5 empty] | BuchholzOil | 38145 | DI | 149 | 1 | Y | A |  |  | For oil filled transformers
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | Word 7 | BIT 1 | PLC | Serial | Buchholz Gas Trip | High | = | Buchhoz Gas Fault | [5 empty] | BuchholzGas | 38146 | DI | 149 | 2 | Y | A |  |  | For oil filled transformers
1500VDC | Rectifier | R1 TX | Rectifier No. 1 |  | Word 7 | BIT 2 | PLC | Serial | Rectifier Tx Over Pressure | High | = | Over Pressure Fault | [5 empty] | OverPressure | 38147 | DI | 149 | 3 | Y | A
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | Word 7 | BIT 3 | PLC | Serial | DC Reverse Current | High | = | Rev Curr Fault | [5 empty] | ReverseCurrent | 38148 | DI | 149 | 4 | Y | A
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | Word 7 | BIT 4 | PLC | Serial | Rectifier frame leakage | High | = | Frame Leak Fault | [5 empty] | FrameLeakage | 38149 | DI | 149 | 5 | Y | A
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | Word 7 | BIT 5 | PLC | Serial | Rectifier Lockout | High | = | CB locked out | [5 empty] | PLC Lockout | 38150 | DI | 149 | 6 |  | A
1500VDC | Rectifier | R1 NEG ISOL | Rectifier No. 1 |  | Word 7 | BIT 6 | PLC | Serial | Negative Isolator Closed | High | = | Neg Isol Closed | [5 empty] | Status(0) | 38151 | DI | 149 | 7 |  | A
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | S1040 | 1 |  | DI | Rectifier MTM Lockout (k86r) | Energised | = | Locked out |  | 1 | 7 | 12 | R1S7DI/12 | Lockout | 1803 | DI | 7 | 11 | Y | A |  | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | IA040 | 1W | X3:7 | AI | DC Circuit Current +ve | 0-20 mA | = | 0 – 13000A |  | 1 | 7 | 33 | R1S7AI/CH33 + | DCCurrent | 1824 | AI | 7 | 32 |  | L |  | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | IA040 | 1B | X3:8 |  | DC Circuit Current -ve |  |  |  |  | 1 | 7 | 33 | R1S7AI/CH33 - | [8 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | IA040 | S |  |  | Screen | [16 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | IA050 | 1W | X3:11 | AI | DC Voltage +ve | 0-20 mA | = | 0 – 2200v |  | 1 | 7 | 34 | R1S7AI/CH34 + | DCVoltage | 1825 | AI | 7 | 33 |  | A | 10 | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | IA050 | 1B | X3:12 |  | DC Voltage -ve |  |  |  |  | 1 | 7 | 34 | R1S7AI/CH34 - | [8 empty] | Y
1500VDC | Rectifier | R1 | Rectifier No. 1 |  | IA050 | S |  |  | Screen | [16 empty] | Y
1500VDC | Rectifier | R1 TX | [15 empty] | Tap Position | 16896 | AI | 66 | 0 |  | L |  |  | Internal to RTU. Analogue representing Tap position
1500VDC | Rectifier | R1 TX |  | 1 | S1008 | 1 |  |  | Control +ve | [7 empty] | R1S10DO/CH8-a | [6 empty] | - |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1008 | 2 |  | PO | Remote Lower Command |  |  |  |  | 1 | 10 | 7 | R1S10DO/CH8-b | Lower | 2566 | PO | 10 | 6 |  | - |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1008 | 3 |  |  | Control +ve | [7 empty] | R1S10DO/CH7-a | [6 empty] | - |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1008 | 4 |  | PO | Remote Raise Command |  |  |  |  | 1 | 10 | 8 | R1S10DO/CH7-b | Raise | 2567 | PO | 10 | 7 |  | - |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 16 |  | DI | MCB Tripped Alarm (Circuit Fail) | Energised | = | MCB Closed |  | 1 | 7 | 13 | R1S7DI/13 | TapChangerSupply | 1803 | DI | 7 | 11 |  | A |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 1 |  | DI | Tap Changer No.1 Motor O/L Trip | Energised | = | Tripped |  | 1 | 7 | 14 | R1S7DI/14 | TC Overload | 1804 | DI | 7 | 12 | Y | A |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 2 |  | DI | Tap Changer No.1 Tap 1 | Energised | = | On Tap 1 |  | 1 | 7 | 15 | R1S7DI/15 | TC POS 1 | 1805 | DI | 7 | 13 |  | L |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 3 |  | DI | Tap Changer No.1 Tap 2 | Energised | = | On Tap 2 |  | 1 | 7 | 16 | R1S7DI/16 | TC POS 2 | 1806 | DI | 7 | 14 |  | L |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 4 |  | DI | Tap Changer No.1 Tap 3 | Energised | = | On Tap 3 |  | 1 | 7 | 17 | R1S7DI/17 | TC POS 3 | 1807 | DI | 7 | 15 |  | L |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 5 |  | DI | Tap Changer No.1 Tap 4 | Energised | = | On Tap 4 |  | 1 | 7 | 18 | R1S7DI/18 | TC POS 4 | 1808 | DI | 7 | 16 |  | L |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 6 |  | DI | Tap Changer No.1 Tap 5 | Energised | = | On Tap 5 |  | 1 | 7 | 19 | R1S7DI/19 | TC POS 5 | 1809 | DI | 7 | 17 |  | L |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 7 |  | DI | Tap Changer No.1 Tap 6 | Energised | = | On Tap 6 |  | 1 | 7 | 20 | R1S7DI/20 | TC POS 6 | 1810 | DI | 7 | 18 |  | L |  | Y
1500VDC | Rectifier | R1 TX |  | 1 | S1034 | 8 |  | DI | Tap Changer No.1 Tap 7 | Energised | = | On Tap 7 |  | 1 | 7 | 21 | R1S7DI/21 | TC POS 7 | 1811 | DI | 7 | 19 |  | L |  | Y
Rectifier DCCB | RDCCB | R1 | Rectifier | 1 | S1015 | 8 | x15:76 | DI | DCCB Open | Energised | = | CB Open |  | 1 | 7 | 22 | R1S7DI/22 | Status(1) | 1812 | DI | 7 | 20 |  | L |  | Y | For non metal clad DCCBs
Rectifier DCCB | RDCCB | R1 | Rectifier | 1 | S1015 | 9 | x15:75 | DI | DCCB Closed | Energised | = | CB Closed |  | 1 | 7 | 23 | R1S7DI/23 | Status(0) | 1813 | DI | 7 | 21 |  | L |  | Y | For non metal clad DCCBs
1500VDC | Rectifier | R1 DCCB | Common Equipment Panel | 2 | S1108 | 1 |  | +ve | 125V dc common
1500VDC | Rectifier | R1 DCCB | Comm Equip Panel or DC SB | 2 | S1108 | 2 |  | DI | 1500V DC Switchboard Frame Leakage Trip | Energised | = | F/L occurred |  | 2 | 3 | 1 | R2S3DI/1 | Frame Leakage | 3840 | DI | 15 | 0 | Y |  |  | Y
1500VDC | Rectifier | R1 DCCB | Comm Equip Panel or DC SB | 2 | S1108 | 3 |  | DI | Frame Leakage Relay Failed | Energised | = | Healthy |  | 2 | 3 | 2 | R2S3DI/2 | Frame Leakage Relay | 3841 | DI | 15 | 1 |  |  |  | Y
1500VDC | Rectifier | R1 DCCB | Comm Equip Panel or DC SB | 2 | S1108 | 4 |  | DI | Frame Leakage Protection Supply Healthy | Energised | = | Volts Present |  | 2 | 3 | 3 | R2S3DI/3 | Frame Leakage Supply | 3842 | DI | 15 | 2 |  |  |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1005 | 1 | X15:01 |  | Control +ve | [7 empty] | R1S11DO/CH2-a | [6 empty] | - |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1005 | 2 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 11 | 2 | R1S11DO/CH2-b | Close | 2817 | PO | 11 | 1 |  | - |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1005 | 3 | X15:02 |  | Control +ve | [7 empty] | R1S11DO/CH1-a | [6 empty] | - |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1005 | 4 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 11 | 1 | R1S11DO/CH1-b | Open | 2816 | PO | 11 | 0 |  | - |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 1 | X15:8 | DI | ACCB Open | Energised | = | CB Open |  | 1 | 7 | 24 | R1S7DI/24 | Status(1) | 1814 | DI | 7 | 22 |  | A |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 2 | X15:9 | DI | ACCB Closed | Energised | = | CB Closed |  | 1 | 7 | 25 | R1S7DI/25 | Status(0) | 1815 | DI | 7 | 23 |  | A |  | Y
33KV | Switch | NO1 33/11KV TX 33KV ISOL | 33kV Panel 33/11 Tx | 1 | S1040 | 3 | X15:10 | DI | Disconnector Open | Energised | = | DISC Open |  | 1 | 7 | 26 | R1S7DI/26 | Status(1) | 1816 | DI | 7 | 24 |  | A |  | Y
33KV | Switch | NO1 33/11KV TX 33KV ISOL | 33kV Panel 33/11 Tx | 1 | S1040 | 4 | X15:11 | DI | Disconnector Closed | Energised | = | DISC Closed |  | 1 | 7 | 27 | R1S7DI/27 | Status(0) | 1817 | DI | 7 | 25 |  | A |  | Y
33KV | Switch | NO1 33/11KV TX 33KV EARTH | 33kV Panel 33/11 Tx | 1 | S1040 | 5 | X15:12 | DI | Earth Switch Open | Energised | = | ES Open |  | 1 | 7 | 28 | R1S7DI/28 | Status(1) | 1818 | DI | 7 | 26 |  | A |  | Y
33KV | Switch | NO1 33/11KV TX 33KV EARTH | 33kV Panel 33/11 Tx | 1 | S1040 | 6 | X15:14 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 1 | 7 | 29 | R1S7DI/29 | Status(0) | 1819 | DI | 7 | 27 |  | A |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 7 | X15:16 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 1 | 7 | 30 | R1S7DI/30 | SpringCharged | 1820 | DI | 7 | 28 |  | A | 10 | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 9 | X15:19 | DI | ILIS Trip | Energised | = | Trip |  | 1 | 7 | 31 | R1S7DI/31 | ILISTrip | 1821 | DI | 7 | 29 | Y | A |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 8 | X15:20 | DI | ILIS Fault | Energised | = | Healthy |  | 1 | 7 | 32 | R1S7DI/32 | ILISFault | 1822 | DI | 7 | 30 |  | A |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | IA020 | W | X3:1 | AI | B Phase AC Current +ve | 0-20 mA | = | 0 – 200 A | 200/1A | 1 | 7 | 35 | R1S7AI/CH35+ | Current | 1826 | AI | 7 | 34 |  | A | 10 | Y | Transducer is 1A/20mA
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | IA020 | B | X3:4 |  | B Phase AC Current -ve |  |  |  |  | 1 | 7 | 35 | R1S7AI/CH35- | [8 empty] | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | IA020 | S |  |  | Screen | [16 empty] | Y
33kV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 10 |  | DI | Low Gas (Stage 1) | Energised | = | Gas Level OK |  | 1 | 8 | 1 | R1S8DI/1 | Low Gas | 2048 | DI | 8 | 0 |  | A |  | Y | Switchgear dependent
33kV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1040 | 11 |  | DI | Low Gas Lockout (Stage 2) | Energised | = | Locked out |  | 1 | 8 | 2 | R1S8DI/2 | Low Gas L/O | 2049 | DI | 8 | 1 | Y | A |  | Y | Switchgear dependent
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx | [6 empty] | Low | = | Comms Healthy | [5 empty] | DiffRelayCommsFail | 37632 | DI | 147 | 0 |  | A | 10 |  | Internal to RTU
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx | 1 | S1041 | 1 | X15:25 | DI | Diff Relay (P632) Watchdog | Energised | = | Relay Healthy |  | 1 | 8 | 3 | R1S8DI/3 | DiffRelayFail | 2050 | DI | 8 | 2 |  | A |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 0 | P632 | Serial | Tx Diff Trip Alarm A | High | = | Fault | [5 empty] | DifferentialTripA | 37633 | DI | 147 | 1 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 1 | P632 | Serial | Tx Diff Trip Alarm B | High | = | Fault | [5 empty] | DifferentialTripB | 37634 | DI | 147 | 2 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 2 | P632 | Serial | Tx Diff Trip Alarm C | High | = | Fault | [5 empty] | DifferentialTripC | 37635 | DI | 147 | 3 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 3 | P632 | Serial | Trip Circuit 1 Supervision Alarm | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 37636 | DI | 147 | 4 |  | A |  |  | Hardwired if from dedicated TC relay.
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 4 | P632 | Serial | CB FAIL Alarm (TC1 – P632) | High | = | CB did not trip – TC1 | [5 empty] | DiffBreakerFail | 37637 | DI | 147 | 5 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 5 | P632 | Serial | Tap Changer Oil Pressure Switch | High | = | Pressure Activated | [5 empty] | TCPressure | 37638 | DI | 147 | 6 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 6 | P632 | Serial | Tap Changer Alarm | High | = | TC Fault | [5 empty] | TCFail | 37639 | DI | 147 | 7 |  | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 7 | P632 | Serial | Buchholz Oil Trip | High | = | Buchholz Oil Fault | [5 empty] | BuchholzOil | 37640 | DI | 147 | 8 | Y | A |  |  | For oil filled transformers
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 8 | P632 | Serial | Buchholz Gas Trip | High | = | Buchholz Gas Fault | [5 empty] | BuchholzGas | 37641 | DI | 147 | 9 | Y | A |  |  | For oil filled transformers
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 9 | P632 | Serial | Tx Pressure Switch | High | = | Over Pressure Fault | [5 empty] | Pressure | 37642 | DI | 147 | 10 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33kV Panel 33/11 Tx |  | WORD-14 | BIT 10 | P632 | Serial | Winding Temp Alarm | High | = | Passed Lower Temp | [5 empty] | TXWdgTempAlarm | 37643 | DI | 147 | 11 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | [6 empty] | Low | = | Comms Healthy | [5 empty] | OverCurrRelayCommFail | 37376 | DI | 146 | 0 |  | A | 10 |  | Internal to RTU
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx | 1 | S1024 | 1 | X15:32 | DI | OC Relay (P127) Watchdog | Energised | = | Relay Healthy |  | 1 | 8 | 2 | R1S8DI/2 | OverCurrentRelay | 2049 | DI | 8 | 1 |  | A |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 0 | P127 | Serial | OC Trip Alarm (A-phase) | High | = | O/C Fault | [5 empty] | OverCurrentA | 37377 | DI | 146 | 1 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 1 | P127 | Serial | OC Trip Alarm (B-phase) | High | = | O/C Fault | [5 empty] | OverCurrentB | 37378 | DI | 146 | 2 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 2 | P127 | Serial | OC Trip Alarm (C-phase) | High | = | O/C Fault | [5 empty] | OverCurrentC | 37379 | DI | 146 | 3 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 3 | P127 | Serial | OC Trip Alarm (AB-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAB | 37380 | DI | 146 | 4 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 4 | P127 | Serial | OC Trip Alarm (AC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAC | 37381 | DI | 146 | 5 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 5 | P127 | Serial | OC Trip Alarm (BC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentBC | 37382 | DI | 146 | 6 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 6 | P127 | Serial | OC Trip Alarm (ABC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentABC | 37383 | DI | 146 | 7 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 7 | P127 | Serial | Earth Fault Trip Alarm | High | = | Earth Fault | [5 empty] | EarthFault | 37384 | DI | 146 | 8 | Y | A
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 8 | P127 | Serial | Trip Circuit 2 Supervision Alarm | Low | = | TC2 Healthy | [5 empty] | TripCircuitSupervision2 | 37385 | DI | 146 | 9 |  | A |  |  | Hardwired if from dedicated TC relay.
33KV | ACCB | NO1 33/11KV TX 33KV | 33kV Panel 33/11 Tx |  | Word 8 | BIT 9 | P127 | Serial | CB Fail Alarm (TC2 – P127) | High | = | CB did not trip – TC2 | [5 empty] | BreakerFailOC | 37386 | DI | 146 | 10 | Y | A
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | IA110 | W |  | AI | Transformer Winding Temp +ve | 0-20 mA | = | 0 - 150°C |  | 1 | 8 | 33 | R1S8AI/CH33 + | TXHotSpotTemp | 2080 | AI | 8 | 32 |  | A | 10 | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | IA110 | B |  |  | Transformer Winding Temp -ve | [7 empty] | R1S8AI/CH33 - | [8 empty] | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | IA110 | S |  |  | Screen | [16 empty] | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | IA111 | W |  | AI | Transformer Oil Temp +ve | 0-20 mA | = | 0 - 150°C |  | 1 | 8 | 34 | R1S8AI/CH34 + | TXTopOilTemp | 2081 | AI | 8 | 33 |  | A | 10 | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | IA111 | B |  |  | Transformer Oil Temp -ve | [7 empty] | R1S8AI/CH34 - | [8 empty] | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | IA111 | S |  |  | Screen | [16 empty] | Y
33KV/11KV | Transformer | NO1 33/11KV 11kV | 33/11kV Tx |  | IA012 | W | X3:6 | AI | 11kV Voltage (C-A Phase) +ve | 0-20 mA | = | 0 – 12.5 kV | 11kV/110V | 1 | 8 | 35 | R1S8AI/CH35 + | Voltage | 2082 | AI | 8 | 34 |  | A | 10 | Y | Transducer is 125V/20mA
33KV/11KV | Transformer | NO1 33/11KV 11kV | 33/11kV Tx |  | IA012 | B | X3:7 |  | 11kV Voltage (C-A Phase) -ve |  |  |  |  | 1 | 8 | 35 | R1S8AI/CH35 - | [8 empty] | Y
33KV/11KV | Transformer | NO1 33/11KV 11kV | 33/11kV Tx |  | IA012 | S | X3:8 |  | Screen | [16 empty] | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 1 |  | DI | Winding Temp Critical Alarm | Energised | = | Passed Critical Temp |  | 1 | 8 | 3 | R1S8DI/3 | TXWdgTempCritical | 2050 | DI | 8 | 2 | Y | A |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 2 |  | DI | Oil Temp Critical Alarm | Energised | = | Passed Critical Temp |  | 1 | 8 | 4 | R1S8DI/4 | TXOilTempCritical | 2051 | DI | 8 | 3 | Y | A |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 5 |  | DI | Oil Temp Alarm | Energised | = | Passed Lower Temp |  | 1 | 8 | 7 | R1S8DI/7 | TXOilTempAlarm | 2054 | DI | 8 | 6 | Y | A |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 6 |  | DI | Main Tank High Oil | Energised | = | Oil Not High Level |  | 1 | 8 | 8 | R1S8DI/8 | TXMainOilHigh | 2055 | DI | 8 | 7 |  | A |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 7 |  | DI | Main Tank Low Oil | Energised | = | Oil Not Low Level |  | 1 | 8 | 9 | R1S8DI/9 | TXMainOilLow | 2056 | DI | 8 | 8 |  | A |  | Y
33KV | ACCB | NO1 33/11KV TX 33KV | 33/11kV Tx | 1 | S1035 | 10 | X15:34 | DI | MTM Relay Lockout (k86t) | Energised | = | Locked out |  | 1 | 8 | 12 | R1S8DI/12 | Lockout | 2059 | DI | 8 | 11 | Y | A |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 11 |  | DI | Fan Motor Running | Energised | = | Fan Running |  | 1 | 8 | 13 | R1S8DI/13 | FanRunning | 2060 | DI | 8 | 12 |  | A |  | Y | Required for Tx's with fans
33KV/11KV | Transformer | NO1 33/11KV TX | 33/11kV Tx | 1 | S1035 | 12 |  | DI | Fan Motor Fault | Energised | = | Fan Fault |  | 1 | 8 | 14 | R1S8DI/14 | FanFail | 2061 | DI | 8 | 13 |  | A |  | Y | Required for Tx's with fans
11KV/415V | Transformer | NO1 11kV/415V TX | 11kV/415V Tx | 1 | S1035 | 13 |  | DI | Temperature monitor fault | Energised | = | Fault |  | 1 | 8 | 15 | R1S8DI/15 | TempFault | 2062 | DI | 8 | 14 |  | A |  | Y | For Tx with temperature monitor device
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1030 | 1 |  | DI | Tap Changer Faulty | Energised | = | Fault |  | 1 | 8 | 16 | R1S8DI/16 | TCFail | 6926 | DI | 8 | 15 | Y |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1030 | 2 |  | DI | Tap Changer Limit | Energised | = | Within Limits |  | 1 | 8 | 17 | R1S8DI/17 | TCLimit | 6927 | DI | 8 | 16 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1030 | 3 |  | DI | Tap Changer Winding Temp Alarm | Energised | = | Passed alarm temp |  | 1 | 8 | 18 | R1S8DI/18 | TCWdgTemp | 6928 | DI | 8 | 17 | Y |  |  | Y | Trip Temp Exceeded - Via ACCB
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1030 | 4 |  | DI | Tap Changer Oil Temp Alarm | Energised | = | Passed alarm temp |  | 1 | 8 | 19 | R1S8DI/19 | TCOilTemp | 6929 | DI | 8 | 18 | Y |  |  | Y | Trip Temp Exceeded - Via ACCB
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1030 | 5 |  | DI | Motor Protection CB Trip Alarm | Energised | = | Closed (No Fault) |  | 1 | 8 | 20 | R1S8DI/20 | TCMotorCB | 6930 | DI | 8 | 19 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1030 | 6 |  | DI | Buchholz Oil Trip | Energised | = | Buchholz Oil Fault |  | 1 | 8 | 21 | R1S8DI/21 | TCBuchholzOil | 37639 | DI | 8 | 20 | Y |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 1 |  | DI | Tap Changer Position Tap 1 | Energised | = | On Tap 1 |  | 2 | 4 | 1 | R2S4DI/1 | Tap position 1 | 4096 | DI | 16 | 0 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 2 |  | DI | Tap Changer Position Tap 2 | Energised | = | On Tap 2 |  | 2 | 4 | 2 | R2S4DI/2 | Tap position 2 | 4097 | DI | 16 | 1 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 3 |  | DI | Tap Changer Position Tap 3 | Energised | = | On Tap 3 |  | 2 | 4 | 3 | R2S4DI/3 | Tap position 3 | 4098 | DI | 16 | 2 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 4 |  | DI | Tap Changer Position Tap 4 | Energised | = | On Tap 4 |  | 2 | 4 | 4 | R2S4DI/4 | Tap position 4 | 4099 | DI | 16 | 3 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 5 |  | DI | Tap Changer Position Tap 5 | Energised | = | On Tap 5 |  | 2 | 4 | 5 | R2S4DI/5 | Tap position 5 | 4100 | DI | 16 | 4 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 6 |  | DI | Tap Changer Position Tap 6 | Energised | = | On Tap 6 |  | 2 | 4 | 6 | R2S4DI/6 | Tap position 6 | 4101 | DI | 16 | 5 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 7 |  | DI | Tap Changer Position Tap 7 | Energised | = | On Tap 7 |  | 2 | 4 | 7 | R2S4DI/7 | Tap position 7 | 4102 | DI | 16 | 6 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 8 |  | DI | Tap Changer Position Tap 8 | Energised | = | On Tap 8 |  | 2 | 4 | 8 | R2S4DI/8 | Tap position 8 | 4103 | DI | 16 | 7 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 9 |  | DI | Tap Changer Position Tap 9 | Energised | = | On Tap 9 |  | 2 | 4 | 9 | R2S4DI/9 | Tap position 9 | 4104 | DI | 16 | 8 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1031 | 10 |  | DI | Tap Changer Position Tap 10 | Energised | = | On Tap 10 |  | 2 | 4 | 10 | R2S4DI/10 | Tap position 10 | 4105 | DI | 16 | 9 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 1 |  | DI | Tap Changer Position Tap 11 | Energised | = | On Tap 11 |  | 2 | 4 | 11 | R2S4DI/11 | Tap position 11 | 4106 | DI | 16 | 10 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 2 |  | DI | Tap Changer Position Tap 12 | Energised | = | On Tap 12 |  | 2 | 4 | 12 | R2S4DI/12 | Tap position 12 | 4107 | DI | 16 | 11 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 3 |  | DI | Tap Changer Position Tap 13 | Energised | = | On Tap 13 |  | 2 | 4 | 13 | R2S4DI/13 | Tap position 13 | 4108 | DI | 16 | 12 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 4 |  | DI | Tap Changer Position Tap 14 | Energised | = | On Tap 14 |  | 2 | 4 | 14 | R2S4DI/14 | Tap position 14 | 4109 | DI | 16 | 13 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 5 |  | DI | Tap Changer Position Tap 15 | Energised | = | On Tap 15 |  | 2 | 4 | 15 | R2S4DI/15 | Tap position 15 | 4110 | DI | 16 | 14 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 6 |  | DI | Tap Changer Position Tap 16 | Energised | = | On Tap 16 |  | 2 | 4 | 16 | R2S4DI/16 | Tap position 16 | 4111 | DI | 16 | 15 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 7 |  | DI | Tap Changer Position Tap 17 | Energised | = | On Tap 17 |  | 2 | 4 | 17 | R2S4DI/17 | Tap position 17 | 4112 | DI | 16 | 16 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 8 |  | DI | Tap Changer Position Tap 18 | Energised | = | On Tap 18 |  | 2 | 4 | 18 | R2S4DI/18 | Tap position 18 | 4113 | DI | 16 | 17 |  |  |  | Y
33KV/11KV | Transformer | NO1 33/11KV TX | Onload Tap Changer | 1 | S1032 | 9 |  | DI | Tap Changer Position Tap 19 | Energised | = | On Tap 19 |  | 2 | 4 | 19 | R2S4DI/19 | Tap position 19 | 4114 | DI | 16 | 18 |  |  |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1005 | 1 | X15:01 |  | Control +ve | [7 empty] | R1S11DO/CH2-a | [6 empty] | - |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1005 | 2 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 11 | 2 | R1S11DO/CH2-b | Close | 2817 | PO | 11 | 1 |  | - |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1005 | 3 | X15:02 |  | Control +ve | [7 empty] | R1S11DO/CH1-a | [6 empty] | - |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1005 | 4 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 11 | 1 | R1S11DO/CH1-b | Open | 2816 | PO | 11 | 0 |  | - |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1040 | 1 | X15:8 | DI | ACCB Open | Energised | = | CB Open |  | 1 | 7 | 24 | R1S7DI/24 | Status(1) | 1814 | DI | 7 | 22 |  | A |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1040 | 2 | X15:9 | DI | ACCB Closed | Energised | = | CB Closed |  | 1 | 7 | 25 | R1S7DI/25 | Status(0) | 1815 | DI | 7 | 23 |  | A |  | Y
11KV | Switch | 11KV HF ISOL | Harmonic Filter ACCB | 1 | S1040 | 3 | X15:10 | DI | Disconnector Open | Energised | = | DISC Open |  | 1 | 7 | 26 | R1S7DI/26 | Status(1) | 1816 | DI | 7 | 24 |  | A |  | Y
11KV | Switch | 11KV HF ISOL | Harmonic Filter ACCB | 1 | S1040 | 4 | X15:11 | DI | Disconnector Closed | Energised | = | DISC Closed |  | 1 | 7 | 27 | R1S7DI/27 | Status(0) | 1817 | DI | 7 | 25 |  | A |  | Y
11KV | Switch | 11KV HF EARTH | Harmonic Filter ACCB | 1 | S1040 | 5 | X15:12 | DI | Earth Switch Open | Energised | = | ES Open |  | 1 | 7 | 28 | R1S7DI/28 | Status(1) | 1818 | DI | 7 | 26 |  | A |  | Y
11KV | Switch | 11KV HF EARTH | Harmonic Filter ACCB | 1 | S1040 | 6 | X15:14 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 1 | 7 | 29 | R1S7DI/29 | Status(0) | 1819 | DI | 7 | 27 |  | A |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1040 | 7 | X15:16 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 1 | 7 | 30 | R1S7DI/30 | SpringCharged | 1820 | DI | 7 | 28 |  | A | 10 | Y | Add delay at Master Station if this comes up while charging
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1040 | 8 | X15:17 | DI | ILIS Trip | Energised | = | Trip |  | 1 | 7 | 31 | R1S7DI/31 | ILISTrip | 1821 | DI | 7 | 29 | Y | A |  | Y | Switchgear dependent
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1040 | 9 | X15:18 | DI | ILIS Fault | Energised | = | Healthy |  | 1 | 7 | 32 | R1S7DI/32 | ILISFault | 1822 | DI | 7 | 30 |  | A |  | Y | Switchgear dependent
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1065 | 10 | X15:22 | DI | Trip Circuit 2 Supervision Alarm | Energised | = | TC 2 Healthy |  | 1 | 7 | 33 | R1S7DI/33 | TripCircuitSupervision2 | 1823 | DI | 7 | 31 |  | A |  | Y | From TC relay 1TM10
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | IA020 | W | X3:1 | AI | B Phase AC Current +ve | 0-20 mA | = | 0 – 200 A | 150/1A | 1 | 7 | 35 | R1S7AI/CH35+ | Current | 1826 | AI | 7 | 34 |  | A | 10 | Y | Transducer is 1A/20mA
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | IA020 | B | X3:4 |  | B Phase AC Current -ve |  |  |  |  | 1 | 7 | 35 | R1S7AI/CH35- | [8 empty] | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | IA020 | S |  |  | Screen | [16 empty] | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | [6 empty] | Low | = | Comms Healthy | [5 empty] | DiffRelayCommFail | 38400 | DI | 150 | 0 |  | A | 10 |  | Internal to RTU
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1061 | 9 | X15:17 | DI | OC & EF Relay (P127) Watchdog | Energised | = | Relay Healthy |  | 1 | 8 | 32 | R1S8DI/32 | OverCurrentRelay | 2078 | DI | 8 | 30 |  | A |  | Y
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 0 | P127 | Serial | OC Trip Alarm (A-phase) | High | = | O/C Fault | [5 empty] | OverCurrentA | 38401 | DI | 150 | 1 | Y | A
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 1 | P127 | Serial | OC Trip Alarm (B-phase) | High | = | O/C Fault | [5 empty] | OverCurrentB | 38402 | DI | 150 | 2 | Y | A
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 2 | P127 | Serial | OC Trip Alarm (C-phase) | High | = | O/C Fault | [5 empty] | OverCurrentC | 38403 | DI | 150 | 3 | Y | A
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 3 | P127 | Serial | Earth Fault Trip Alarm | High | = | Earth Fault | [5 empty] | EarthFault | 38404 | DI | 150 | 4 | Y | A
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 4 | P127 | Serial | Phase undervoltage trip alarm | High | = | Undervoltage Trip | [5 empty] | UnderVoltage | 38405 | DI | 150 | 5 | Y | A |  |  | Switchgear dependent
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 5 | P127 | Serial | Trip Circuit 1 Supervision Alarm | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 38406 | DI | 150 | 6 |  | A
11KV | ACCB | 11KV HF | Harmonic Filter ACCB |  | WORD-20 | BIT 6 | P127 | Serial | CB Fail Alarm (TC1 or TC2) | High | = | CB did not trip | [5 empty] | CB Fail (OC) | 38407 | DI | 150 | 7 |  | A
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | [6 empty] | Low | = | Comms Healthy | [5 empty] | RLC04_1 CommsFail | 38656 | DI | 151 | 0 |  | A | 10
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1068 | 1 | RLC04 | DI | Relay1 watchdog alarm | Energised | = | Relay Healthy |  | 1 | 6 | 1 | R1S6DI/1 | RLC04_1 RelayFail | 2048 | DI | 8 | 0 |  | A |  | Y | RLC04 (1)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1068 | 2 | RLC04 | DI | Repetitive Peak Overvolts/Thermal OC | High | = | O/volts/OC Fault | [5 empty] | Overvolts/OC | 38657 | DI | 151 | 1 |  | A |  |  | RLC04 (1)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1068 | 3 | RLC04 | DI | Thermal overcurrent | High | = | Thermal OC | [5 empty] | Thermal OC | 38658 | DI | 151 | 2 |  | A |  |  | RLC04 (1)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1068 | 3 | RLC04 | DI | Double star unbalance alarm | High | = | Double star Fault | [5 empty] | StarUnbalance | 38659 | DI | 151 | 3 |  | A |  |  | RLC04 (1)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1068 | 4 | RLC04 | DI | CB Fail alarm 1 | High | = | CB did not trip | [5 empty] | RLC04_1 CB Fail | 38660 | DI | 151 | 4 |  | A |  |  | RLC04 (1)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | [6 empty] | Low | = | Comms Healthy | [5 empty] | RLC04_2 CommsFail | 38912 | DI | 152 | 0 |  | A | 10 |  | RLC04 (2)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1069 | 1 | RLC04 | DI | Relay2 watchdog alarm | Energised | = | Relay Healthy |  | 1 | 6 | 2 | R1S6DI/2 | RLC04_2 RelayFail | 2049 | DI | 8 | 1 |  | A |  | Y | RLC04 (2)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1069 | 2 | RLC04 | DI | CB Fail alarm 2 (Relay 2) | High | = | CB did not trip | [5 empty] | RLC04_2 CB Fail | 38914 | DI | 152 | 2 |  | A |  |  | RLC04 (2)
11KV | ACCB | 11KV HF | Harmonic Filter ACCB | 1 | S1069 | 3 | RLC04 | DI | H-Bridge unbalance alarm (Relay 2) | High | = | Hbridge Fault | [5 empty] | RLC04_2 Hbridge | 38915 | DI | 152 | 3 |  | A |  |  | RLC04 (2)
11KV | Switch | 6XX | 11kV Feeder Switch | 1 | S1007 | 1 | X15:01 |  | Control +ve | [7 empty] | R1S11DO/CH6-a | [6 empty] | - |  | Y | Use of 11kV switch remote control is restricted
11KV | Switch | 6XX | 11kV Feeder Switch | 1 | S1007 | 2 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 11 | 6 | R1S11DO/CH6-b | Close | 2823 | PO | 11 | 7 |  | - |  | Y | Use of 11kV switch remote control is restricted
11KV | Switch | 6XX | 11kV Feeder Switch | 1 | S1008 | 3 | X15:02 |  | Control +ve | [7 empty] | R1S11DO/CH7-a | [6 empty] | - |  | Y | Use of 11kV switch remote control is restricted
11KV | Switch | 6XX | 11kV Feeder Switch | 1 | S1009 | 4 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 11 | 7 | R1S11DO/CH7-b | Open | 2822 | PO | 11 | 6 |  | - |  | Y | Use of 11kV switch remote control is restricted
11KV | Switch | 6XX | 11kV Feeder Switch | 1 | S1048 | 1 | X15:8 | DI | Switch Open | Energised | = | Switch Open |  | 1 | 7 | 15 | R1S7DI/15 | Status(1) | 1808 | DI | 7 | 16 |  | A |  | Y
11KV | Switch | 6XX | 11kV Feeder Switch | 1 | S1048 | 2 | X15:9 | DI | Switch Closed | Energised | = | Switch Closed |  | 1 | 7 | 16 | R1S7DI/16 | Status(0) | 1807 | DI | 7 | 15 |  | A |  | Y
11KV | VT | 11KV VT NO1 | 11kV Feeder Panel | 1 | S1063 | 1 |  | +VE | 125V dc common | [16 empty] | Y | The VT may be in the feeder panel, but the master station associates it with the bus section.
11KV | VT | 11KV VT NO1 | 11kV Feeder Panel | 1 | S1063 | 3 | X15:29 | DI | Phase Failure (K47) | Energised | = | Healthy |  | 1 | 8 | 17 | R1S8DI/17 | PhaseFailure | 2064 | DI | 8 | 16 |  | A |  | Y | VT may be in feeder panel, but the master station associates it with the bus section.
11KV | VT | 11KV VT NO1 | 11kV Feeder Panel |  | IA010 | W | X3:6 | AI | Busbar Voltage (C-A Phase) +ve | 0-20 mA | = | 0 – 37.5 kV | 33kV/110V | 1 | 8 | 35 | R1S8AI/CH35 + | Voltage | 2082 | AI | 8 | 34 |  | A | 10 | Y | Transducer is 125V/20mA
11KV | VT | 11KV VT NO1 | 11kV Feeder Panel |  | IA010 | B | X3:7 |  | Busbar Voltage (C-A Phase) -ve |  |  |  |  | 1 | 8 | 35 | R1S8AI/CH35 - | [8 empty] | Y
11KV | VT | 11KV VT NO1 | 11kV Feeder Panel |  | IA011 | S | X3:8 |  | Screen | [16 empty] | Y
66KV | VT | 66KV VT NO1 | 66kV Feeder Panel | 1 | S1045 | 1 |  | DI | Disconnector Open | Energised | = | DISC Open |  | 1 | 8 | 18 | R1S8DI/18 | Open | 2065 | DI | 8 | 17 |  |  |  | Y | Only 66kV switchgear
66KV | VT | 66KV VT NO1 | 66kV Feeder Panel | 1 | S1045 | 2 |  | DI | Disconnector Closed | Energised | = | DISC Closed |  | 1 | 8 | 19 | R1S8DI/19 | Closed | 2066 | DI | 8 | 18 |  |  |  | Y | Only 66kV switchgear
66KV | VT | 66KV VT NO1 | 66kV Feeder Panel | 1 | S1045 | 3 |  | DI | VT Healthy | Energised | = | VT Healthy |  | 1 | 8 | 20 | R1S8DI/20 | VT | 2067 | DI | 8 | 19 |  |  |  | Y | Only 66kV switchgear
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1050 | 1 | X15:01 |  | Control +ve | [7 empty] | R1S11DO/CH6-a | [6 empty] | - |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1050 | 2 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 11 | 6 | R1S11DO/CH6-b | Close | 2821 | PO | 11 | 5 |  | - |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1050 | 3 | X15:02 |  | Control +ve | [7 empty] | R1S11DO/CH5-a | [6 empty] | - |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1050 | 4 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 11 | 5 | R1S11DO/CH5-b | Open | 2820 | PO | 11 | 4 |  | - |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1061 | 1 | X15:08 | DI | ACCB Open | Energised | = | CB Open |  | 1 | 8 | 18 | R1S8DI/18 | Status(1) | 2065 | DI | 8 | 17 |  | A |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1061 | 2 | X15:09 | DI | ACCB Closed | Energised | = | CB Closed |  | 1 | 8 | 19 | R1S8DI/19 | Status(0) | 2066 | DI | 8 | 18 |  | A |  | Y
11KV | Switch | 6XX ISOL | 11kV Feeder Panel | 1 | S1061 | 3 | X15:10 | DI | Disconnector Open | Energised | = | DISC Open |  | 1 | 8 | 20 | R1S8DI/20 | Status(1) | 2067 | DI | 8 | 19 |  | A |  | Y | The 3 position switch is presented as 2 position switches
11KV | Switch | 6XX ISOL | 11kV Feeder Panel | 1 | S1061 | 4 | X15:11 | DI | Disconnector Closed | Energised | = | DISC Closed |  | 1 | 8 | 21 | R1S8DI/21 | Status(0) | 2068 | DI | 8 | 20 |  | A |  | Y
11KV | Switch | 6XX EARTH | 11kV Feeder Panel | 1 | S1061 | 5 | X15:12 | DI | Earth Switch Open | Energised | = | ES Open |  | 1 | 8 | 22 | R1S8DI/22 | Status(1) | 2069 | DI | 8 | 21 |  | A |  | Y
11KV | Switch | 6XX EARTH | 11kV Feeder Panel | 1 | S1061 | 6 | X15:13 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 1 | 8 | 23 | R1S8DI/23 | Status(0) | 2070 | DI | 8 | 22 |  | A |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1061 | 7 | X15:14 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 1 | 8 | 24 | R1S8DI/24 | SpringCharged | 2071 | DI | 8 | 23 |  | A | 10 | Y | Add delay at Master Station if this comes up while charging
11KV | ACCB | 6XX | 11kV Feeder Panel |  | IA070 | W | X3:1 | AI | B Phase AC Current +ve | 0-20 mA | = | 0 - 300 A | 300/1A | 1 | 8 | 36 | R1S8AI/CH36+ | Current | 2083 | AI | 8 | 35 |  | A | 10 | Y | Transducer is 1A/20mA
11KV | ACCB | 6XX | 11kV Feeder Panel |  | IA070 | B | X3:4 |  | B Phase AC Current -ve |  |  |  |  | 1 | 8 | 36 | R1S8AI/CH36- | [8 empty] | Y
11KV | ACCB | 6XX | 11kV Feeder Panel |  | IA070 | S |  |  | Screen | [16 empty] | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1070 | 1 |  | DI | Low Gas (Stage 1) | Energised | = |  |  | 1 | 8 | 25 | R1S8DI/25 | LowGas | 2072 | DI | 8 | 24 |  | A |  | Y | Required for gas CBs
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1070 | 2 |  | DI | Low Gas Lockout (Stage 2) | Energised | = |  |  | 1 | 8 | 26 | R1S8DI/26 | LowGasLockout | 2073 | DI | 8 | 25 | Y | A |  | Y | Required for gas CBs
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1070 | 3 |  | DI | Motor Fault | Energised | = | Motor Healthy |  | 1 | 8 | 27 | R1S8DI/27 | MotorTrouble | 2074 | DI | 8 | 26 |  | A |  | Y | Required for gas CBs
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1070 | 4 |  | DI | Motor Protection CB Trip Alarm | Energised | = |  |  | 1 | 8 | 28 | R1S8DI/28 | MotorSupply | 2075 | DI | 8 | 27 |  | A |  | Y | Required for gas CBs
11KV | Switch | 6XX EARTH | 11kV Feeder Panel | 1 | S1061 | 11 | X15:18 | DI | Disconnector Earthed | Energised | = | Disc Earthed |  | 1 | 8 | 29 | R1S8DI/29 | Status (2) | 2076 | DI | 8 | 28 |  | A |  | Y | Only required for 3 position switches
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1061 | 8 | X15:15 | DI | PW Relay (P521) Watchdog | Energised | = | Relay Healthy |  | 1 | 8 | 30 | R1S8DI/30 | PWRelayFail | 2077 | DI | 8 | 29 |  | A |  | Y | Protection scheme may prescribe this
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1061 | 9 | X15:16 | DI | OC & EF Relay (P127) Watchdog | Energised | = | Relay Healthy |  | 1 | 8 | 31 | R1S8DI/31 | OverCurrentRelay | 2078 | DI | 8 | 30 |  | A |  | Y | Protection scheme may prescribe this
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1061 | 10 | X15:17 | DI | DOC & DEF Voltage Healthy (CB Q2x closed) | Energised | = | Volts Present |  | 1 | 8 | 32 | R1S8DI/32 | DirProtVolts | 2079 | DI | 8 | 31 |  | A |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1065 | 1 | X15:19 | DI | Pilot Wire Trip | Energised | = | Fault on feeder |  | 1 | 4 | 20 | R1S4DI/20 | PilotWireTrip | 4115 | DI | 16 | 19 | Y | A |  | Y | For 11kV hardwired summary alarms are normally required
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1065 | 2 | X15:20 | DI | DOC Trip | Energised | = | O/C Fault |  | 1 | 4 | 21 | R1S4DI/21 | OverCurrent | 4116 | DI | 16 | 20 | Y | A |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1065 | 3 | X15:21 | DI | Trip Circuit 1 Supervision Alarm | Energised | = | TC 1 Healthy |  | 1 | 4 | 22 | R1S4DI/22 | TripCircuitSupervision1 | 4117 | DI | 16 | 21 |  | A |  | Y | From TC relay
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1065 | 4 | X15:22 | DI | Trip Circuit 2 Supervision Alarm | Energised | = | TC 2 Healthy |  | 1 | 4 | 23 | R1S4DI/23 | TripCircuitSupervision2 | 4118 | DI | 16 | 22 |  | A |  | Y | From TC relay
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1065 | 5 | X15:23 | DI | CB Fail Alarm (K187L CB) | Energised | = | CB did not trip – TC1 |  | 1 | 4 | 24 | R1S4DI/24 | BreakerFailPW | 4119 | DI | 16 | 23 | Y | A |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | 1 | S1065 | 6 | X15:24 | DI | CB Fail Alarm (K67 CB) | Energised | = | CB did not trip – TC2 |  | 1 | 4 | 25 | R1S4DI/25 | BreakerFailOC | 4120 | DI | 16 | 24 | Y | A |  | Y
11KV | ACCB | 6XX | 11kV Feeder Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | PWRelayCommsFail | 37888 | DI | 148 | 0 |  | A | 10 |  | Internal to RTU
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 0 | P521 | Serial | Pilot Wire Trip Alarm (A-Phase) | High | = | PW Fault | [5 empty] | PWTripA | 37889 | DI | 148 | 1 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 1 | P521 | Serial | Pilot Wire Trip Alarm (B-Phase) | High | = | PW Fault | [5 empty] | PWTripB | 37890 | DI | 148 | 2 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 2 | P521 | Serial | Pilot Wire Trip Alarm (C-Phase) | High | = | PW Fault | [5 empty] | PWTripC | 37891 | DI | 148 | 3 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 3 | P521 | Serial | Pilot Wire Trip Alarm (AB-Phase) | High | = | PW Fault | [5 empty] | PWTripAB | 37892 | DI | 148 | 4 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 4 | P521 | Serial | Pilot Wire Trip Alarm (AC-Phase) | High | = | PW Fault | [5 empty] | PWTripAC | 37893 | DI | 148 | 5 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 5 | P521 | Serial | Pilot Wire Trip Alarm (BC-Phase) | High | = | PW Fault | [5 empty] | PWTripBC | 37894 | DI | 148 | 6 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 6 | P521 | Serial | Pilot Wire Trip Alarm (ABC-Phase) | High | = | PW Fault | [5 empty] | PWTripABC | 37895 | DI | 148 | 7 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 7 | P521 | Serial | Trip Circuit 1 Supervision Alarm | Low | = | TC1 Healthy | [5 empty] | TripCircuitSupervision1 | 37896 | DI | 148 | 8 |  | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 8 | P521 | Serial | CB Fail Alarm (TC1 – P521) | High | = | CB did not trip – TC1 | [5 empty] | BreakerFailPW | 37897 | DI | 148 | 9 | Y | A
11KV | Feeder | 6XX | 11kV Feeder Panel |  | WORD-16 | BIT 9 | P521 | Serial | Pilot Communications Failed | High | = | Comms Failed | [5 empty] | PilotWireFail | 37898 | DI | 148 | 10 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel | [6 empty] | Low | = | Comms Healthy | [5 empty] | OverCurrRelayCommFail | 38144 | DI | 149 | 0 |  | A | 10 |  | Internal to RTU
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 0 | P127 | Serial | OC Trip Alarm (A-phase) | High | = | O/C Fault | [5 empty] | OverCurrentA | 38145 | DI | 149 | 1 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 1 | P127 | Serial | OC Trip Alarm (B-phase) | High | = | O/C Fault | [5 empty] | OverCurrentB | 38146 | DI | 149 | 2 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 2 | P127 | Serial | OC Trip Alarm (C-phase) | High | = | O/C Fault | [5 empty] | OverCurrentC | 38147 | DI | 149 | 3 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 3 | P127 | Serial | OC Trip Alarm (AB-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAB | 38148 | DI | 149 | 4 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 4 | P127 | Serial | OC Trip Alarm (AC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAC | 38149 | DI | 149 | 5 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 5 | P127 | Serial | OC Trip Alarm (BC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentBC | 38150 | DI | 149 | 6 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 6 | P127 | Serial | OC Trip Alarm (ABC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentABC | 38151 | DI | 149 | 7 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 7 | P127 | Serial | EF Trip Alarm | High | = | Earth Fault | [5 empty] | OverCurEarthLeakTrip | 38152 | DI | 149 | 8 | Y | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 8 | P127 | Serial | Trip Circuit 2 Supervision Alarm | Low | = | TC2 Healthy | [5 empty] | TripCircuitSupervision2 | 38153 | DI | 149 | 9 |  | A
11KV | ACCB | 6XX | 11kV Feeder Panel |  | WORD-17 | BIT 9 | P127 | Serial | CB FAIL Alarm (TC2 – P127) | High | = | CB did not trip – TC2 | [5 empty] | BreakerFailOC | 38154 | DI | 149 | 10 | Y | A
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1055 | 1 | X15:01 |  | Control +ve | [7 empty] | R1S11DO/CH8-a | [6 empty] | - |  | Y
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1055 | 2 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 11 | 8 | R1S11DO/CH8-b | Close | 2823 | PO | 11 | 7 |  | - |  | Y
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1055 | 3 | X15:02 |  | Control +ve | [7 empty] | R1S11DO/CH7-a | [6 empty] | - |  | Y
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1055 | 4 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 11 | 7 | R1S11DO/CH7-b | Open | 2822 | PO | 11 | 6 |  | - |  | Y
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1070 | 1 | X15:08 | DI | ACCB Open | Energised | = | CB Open |  | 2 | 4 | 26 | R2S4DI/26 | Status(1) | 4121 | DI | 16 | 25 |  | A |  | Y
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1070 | 2 | X15:09 | DI | ACCB Closed | Energised | = | CB Closed |  | 2 | 4 | 27 | R2S4DI/27 | Status(0) | 4122 | DI | 16 | 26 |  | A |  | Y
11KV | Switch | Tx or BS ISOL | Tx or BS ACCB | 1 | S1070 | 3 | X15:10 | DI | Disconnector Open | Energised | = | Disc Open |  | 2 | 4 | 28 | R2S4DI/28 | Status(1) | 4123 | DI | 16 | 27 |  | A |  | Y | The 3 position switch is presented as 2 position switches
11KV | Switch | Tx or BS ISOL | Tx or BS ACCB | 1 | S1070 | 4 | X15:11 | DI | Disconnector Closed | Energised | = | Disc Closed |  | 2 | 4 | 29 | R2S4DI/29 | Status(0) | 4124 | DI | 16 | 28 |  | A |  | Y
11KV | Switch | Tx or BS EARTH | Tx or BS ACCB | 1 | S1070 | 5 | X15:12 | DI | Earth Switch Open | Energised | = | ES Open |  | 2 | 4 | 30 | R2S4DI/30 | Status(1) | 4125 | DI | 16 | 29 |  | A |  | Y
11KV | Switch | Tx or BS EARTH | Tx or BS ACCB | 1 | S1070 | 6 | X15:13 | DI | Earth Switch Closed | Energised | = | ES Closed |  | 2 | 4 | 31 | R2S4DI/31 | Status(0) | 4126 | DI | 16 | 30 |  | A |  | Y
11KV | ACCB | Tx or BS | Tx or BS ACCB | 1 | S1070 | 7 | X15:14 | DI | CB Motor Spring Charged | Energised | = | Charged |  | 2 | 4 | 32 | R2S4DI/32 | SpringCharged | 4127 | DI | 16 | 31 |  | A | 10 | Y | Add delay at Master Station if this comes up while charging
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB | 1 | S1070 | 10 | X15:17 | DI | OC Relay (P127) Watchdog | Energised | = | Relay Healthy |  | 2 | 5 | 1 | R2S5DI/1 | OverCurrentRelay | 4352 | DI | 17 | 0 |  | A |  | Y
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB | 1 | S1070 | 11 | X15:18 | DI | Trip Circuit 1 Supervision Alarm | Energised | = | TC1 Healthy |  | 2 | 5 | 2 | R2S5DI/2 | TripCircuitSupervision1 | 4353 | DI | 17 | 1 |  | A |  | Y | from 1TM10
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | IA080 | W | X3:1 | AI | B Phase AC Current +ve | 0-20 mA | = | 0 - 300 A | 300/1A | 2 | 3 | 33 | R2S3AI/CH33+ | Current | 3872 | AI | 15 | 32 |  | A | 10 | Y
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | IA080 | B | X3:4 |  | B Phase AC Current -ve |  |  |  |  | 2 | 3 | 33 | R2S3AI/CH33- | [8 empty] | Y
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | IA080 | S |  |  | Screen | [16 empty] | Y
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB | [6 empty] | Low | = | Comms Healthy | [5 empty] | DiffRelayCommFail | 38400 | DI | 150 | 0 |  | A | 10 |  | Internal to RTU
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 0 | P127 | Serial | OC Trip Alarm (A-phase) | High | = | O/C Fault | [5 empty] | OverCurrentA | 38401 | DI | 150 | 1 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 1 | P127 | Serial | OC Trip Alarm (B-phase) | High | = | O/C Fault | [5 empty] | OverCurrentB | 38402 | DI | 150 | 2 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 2 | P127 | Serial | OC Trip Alarm (C-phase) | High | = | O/C Fault | [5 empty] | OverCurrentC | 38403 | DI | 150 | 3 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 3 | P127 | Serial | OC Trip Alarm (AB-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAB | 38404 | DI | 150 | 4 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 4 | P127 | Serial | OC Trip Alarm (AC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentAC | 38405 | DI | 150 | 5 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 5 | P127 | Serial | OC Trip Alarm (BC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentBC | 38406 | DI | 150 | 6 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 6 | P127 | Serial | OC Trip Alarm (ABC-phase) | High | = | O/C Fault | [5 empty] | OverCurrentABC | 38407 | DI | 150 | 7 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 7 | P127 | Serial | Neutral Leakage Trip | High | = | Neutral Fault | [5 empty] | NeutralLeakageProt | 38408 | DI | 150 | 8 | Y | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 8 | P127 | Serial | Trip Circuit 2 Supervision Alarm | Low | = | TC2 Healthy | [5 empty] | TripCircuitSupervision2 | 38409 | DI | 150 | 9 |  | A
11KV | ACCB | NO1 33/11KV TX 11KV | 33/11 11kV ACCB |  | WORD-20 | BIT 9 | P127 | Serial | CB Fail Alarm (TC1 or TC2) | High | = | CB did not trip | [5 empty] | BreakerFailOC | 38410 | DI | 150 | 10 |  | A
11KV | ACCB | 11KV 1-2 BS | BT ACCB | 1 | S1066 | 2 |  | DI | Bus Tie Protection MTM Trip | Energised | = | Busbar Fault |  | 2 | 5 | 6 | R2S5DI/6 | Lockout | 4357 | DI | 17 | 5 | Y | A |  | Y
11KV | ACCB | 11KV 1-2 BS | BT ACCB | 1 | S1066 | 6 |  | DI | Trip Circuit 1 Supervision Alarm | Energised | = | TC1 Healthy |  | 2 | 5 | 8 | R2S5DI/8 | TripCircuitSupervision1 | 4359 | DI | 17 | 7 |  | A |  | Y | from 1TM10 Relay
11KV | ACCB | 11KV 1-2 BS | BT ACCB | 1 | S1066 | 7 |  | DI | Trip Circuit 2 Supervision Alarm | Energised | = | TC2 Healthy |  | 2 | 5 | 9 | R2S5DI/9 | TripCircuitSupervision2 | 4360 | DI | 17 | 8 |  | A |  | Y | from 1TM10 Relay
11KV | ACCB | 11KV 1-2 BS | BT ACCB | 1 | S1066 | 10 |  | DI | Differential Trip Alarm (A-Phase) | Energised | = | Diff Fault |  | 2 | 5 | 13 | R2S5DI/13 | DifferentialTripA | 4364 | DI | 17 | 12 | Y | A |  | Y | from MCAG34 Relay
11KV | ACCB | 11KV 1-2 BS | BT ACCB | 1 | S1066 | 11 |  | DI | Differential Trip Alarm (B-Phase) | Energised | = | Diff Fault |  | 2 | 5 | 14 | R2S5DI/14 | DifferentialTripB | 4365 | DI | 17 | 13 | Y | A |  | Y | from MCAG34 Relay
11KV | ACCB | 11KV 1-2 BS | BT ACCB | 1 | S1066 | 12 |  | DI | Differential Trip Alarm (C-Phase) | Energised | = | Diff Fault |  | 2 | 5 | 15 | R2S5DI/15 | DifferentialTripC | 4366 | DI | 17 | 14 | Y | A |  | Y | from MCAG34 Relay
1500VDC | BARCB | 481 | DCCB | 2 |  |  | X15:01 |  | Control +ve | [7 empty] | R1S12DO/CH2-a | [6 empty] | - |  | Y | Half DCCBs on No.1 battery, others No.2
1500VDC | BARCB | 481 | DCCB | 2 | S1101 | 1 | X15:03 | PO | Remote Close Command |  |  |  |  | 1 | 12 | 2 | R1S12DO/CH2-b | Close | 3073 | PO | 12 | 1 |  | - |  | Y
1500VDC | BARCB | 481 | DCCB | 2 |  |  | X15:02 |  | Control +ve | [7 empty] | R1S12DO/CH1-a | [6 empty] | - |  | Y
1500VDC | BARCB | 481 | DCCB | 2 | S1101 | 2 | X15:04 | PO | Remote Open Command |  |  |  |  | 1 | 12 | 1 | R1S12DO/CH1-b | Open | 3072 | PO | 12 | 0 |  | - |  | Y
1500VDC | BARCB | 481 | DCCB | 2 | S1105 | 1 | D | DI | DCCB Open | Energised | = | Open |  | 2 | 3 | 4 | R2S3DI/4 | Status(1) | 3843 | DI | 15 | 3 |  | A |  | Y
1500VDC | BARCB | 481 | DCCB | 2 | S1105 | 2 | C | DI | DCCB Closed | Energised | = | Closed |  | 2 | 3 | 5 | R2S3DI/5 | Status(0) | 3844 | DI | 15 | 4 |  | A |  | Y
1500VDC | BARCB | 481 | DCCB | 2 | S1105 | 21 | 20 | DI | DC Prot Fail | Energised | = | Relay Healthy |  | 2 | 3 | 23 | R2S3DI/23 | DC Prot Fail | 3862 | DI | 15 | 22 |  | A |  | Y | From interface panel for IT or from DCCB with no IT
1500VDC | BARCB | 481 | DCCB | 3 | S1105 | 22 | 21 | DI | Protection relay trip alarm | Energised | = | Prot trip signal |  | 2 | 3 | 24 | R2S3DI/24 | Protection Relay Trip | 3863 | DI | 15 | 23 |  | A |  | Y
1500VDC | BARCB | 481 | DCCB |  | WORD-21 | BIT 0 | UMLe | Serial | Overcurrent trip | High | = | Fault | [5 empty] | OC TRIP | 38656 | DI | 151 | 0 |  | L
1500VDC | BARCB | 481 | DCCB |  | WORD-21 | BIT 1 | UMLe | Serial | Delta-I Relay Operated | High | = | Fault | [5 empty] | Delta I | 38657 | DI | 151 | 1 |  | L
1500VDC | BARCB | 481 | DCCB |  | WORD-21 | BIT 2 | UMLe | Serial | Transducer fail | High | = | Fault | [5 empty] | TransducerFail | 38656 | DI | 151 | 0 |  | A
1500VDC | BARCB | 481 | DCCB |  | WORD-22 | BIT 0 | UMLe | Serial | DC Feeder Current | ±20mA | = | -8000 to 8000A | 8000A/100mV |  |  |  |  | Current | 38945 | AI | 152 | 33 |  | L |  |  | Transducer is 90mV/20mA with
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 |  | 1 | X1:11 | PO | Control +ve | [7 empty] | R1S12DO/CH4-a | [6 empty] | - |  | Y
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1150 | 2 | X1:12 |  | Remote Enable IT Command |  |  |  |  | 1 | 12 | 4 | R1S12DO/CH4-b | ITEnable | 3075 | PO | 12 | 3 |  | - |  | Y
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 |  | 3 | X1:9 | PO | Control +ve | [7 empty] | R1S12DO/CH3-a | [6 empty] | - |  | Y
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1150 | 4 | X1:10 |  | Remote Disable IT Command |  |  |  |  | 1 | 12 | 3 | R1S12DO/CH3-b | ITDisable | 3074 | PO | 12 | 2 |  | - |  | Y
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1151 | 1 | X0:13 | DI | Intertrip 12V supply 1 | Energised | = | Volts present |  | 2 | 6 | 5 | R2S6DI/5 | IT PSU A FAIL | 4612 | DI | 18 | 4 |  | A |  | Y | Supply for all dc feeders
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1151 | 2 | X0:21 | DI | Intertrip 12V supply 2 | Energised | = | Volts present |  | 2 | 6 | 6 | R2S6DI/6 | IT PSU B FAIL | 4613 | DI | 18 | 5 |  | A |  | Y | Supply for all dc feeders
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1151 | 4 | X1:18 | DI | Intertrip scheme comms A health | Energised | = | Healthy |  | 2 | 6 | 8 | R2S6DI/8 | IT COMMS A | 4615 | DI | 18 | 7 |  | A | 10 | Y
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1151 | 5 | X1:19 | DI | Intertrip scheme comms B health | Energised | = | Healthy |  | 2 | 6 | 9 | R2S6DI/9 | IT COMMS B | 4616 | DI | 18 | 8 |  | A | 10 | Y
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1151 | 6 | X1:20 | DI | Intertrip scheme status (switch settings) | Energised | = | Enabled (High setting) |  | 2 | 6 | 10 | R2S6DI/10 | IT Status | 4617 | DI | 18 | 9 |  | A |  | Y | Disabled=Low Trip Settings
1500VDC | BARCB | 481 | Intertrip Interface Panel | 2 | S1151 | 7 | X1:21 | DI | Intertrip relay or transducer fail | Energised | = | Protection Healthy |  | 2 | 6 | 11 | R2S6DI/12 | DC Prot Relay Fail | 4619 | DI | 18 | 10 |  | A |  | Y | From interface panel for IT or from DCCB with no IT
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 |  |  | 43 |  | Control +ve | [7 empty] | R1S12DO/CH2-a | [6 empty] | - |  | Y | Half DCCBs on No.1 battery, others No.2
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1102 | 1 | 45 | PO | Remote Close Command |  |  |  |  | 1 | 12 | 2 | R1S12DO/CH2-b | Close | 3073 | PO | 12 | 1 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 |  |  | 44 |  | Control +ve | [7 empty] | R1S12DO/CH1-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1102 | 2 | 46 | PO | Remote Open Command |  |  |  |  | 1 | 12 | 1 | R1S12DO/CH1-b | Open | 3072 | PO | 12 | 0 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 1 | 57 | DI | DCCB Open | Energised | = | Open |  | 2 | 3 | 4 | R2S3DI/4 | Status(1) | 3843 | DI | 15 | 3 |  | L |  | Y | No alarm except when auto reclose fails
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 2 | 58 | DI | DCCB Closed | Energised | = | Closed |  | 2 | 3 | 5 | R2S3DI/5 | Status(0) | 3844 | DI | 15 | 4 |  | L |  | Y | No alarm except when auto reclose fails
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 |  |  | 53 |  | Control +ve | [7 empty] | R1S12DO/CH4-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1102 | 3 | 56 | PO | Disconnector 'to positive' |  |  |  |  | 1 | 12 | 4 | R1S12DO/CH4-b | To positive | 3075 | PO | 12 | 3 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 |  |  | 54 |  | Control +ve | [7 empty] | R1S12DO/CH3-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1102 | 4 | 55 | PO | Disconnector 'to rail' |  |  |  |  | 1 | 12 | 3 | R1S12DO/CH3-b | To rail | 3074 | PO | 12 | 2 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 4 | 59 | DI | Disconnector 'to rail' | Energised | = | To rail |  | 2 | 3 | 6 | R2S3DI/6 | Status(1) | 3845 | DI | 15 | 5 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 5 | 60 | DI | Disconnector to 'positive' | Energised | = | To positive |  | 2 | 3 | 7 | R2S3DI/7 | Status(0) | 3846 | DI | 15 | 6 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 |  |  | 48 |  | Control +ve | [7 empty] | R1S12DO/CH5-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1102 | 5 | 51 | PO | Line Test Activate |  |  |  |  | 1 | 12 | 5 | R1S12DO/CH5-b | Close | 3076 | PO | 12 | 4 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 |  |  | 49 |  | Control +ve | [7 empty] | R1S12DO/CH6-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1102 | 7 | 52 | PO | Protection L/O Reset |  |  |  |  | 1 | 12 | 7 | R1S12DO/CH7-b | Close | 3078 | PO | 12 | 6 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 8 | 14 | DI | DAOL/CBCM trip | Energised | = | Tripped |  | 2 | 3 | 10 | R2S3DI/10 | DAOL/CBCM Trip | 3849 | DI | 15 | 9 | Y | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB |  | IA140 | W | 61 | AI | DC Feeder Current +ve | 4-20mA | = | -8000 to 8000A |  | 2 | 3 | 34 | R2S3AI/CH34+ | Current | 3873 | AI | 15 | 33 |  | L |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB |  | IA140 | B | 62 |  | DC Feeder Current -ve |  |  |  |  | 2 | 3 | 34 | R2S3AI/CH34- | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB |  | IA140 | S | 63 |  | Screen | [14 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 9 | 10 | DI | OHW alive | Energised | = | OHW alive |  | 2 | 3 | 11 | R2S3DI/11 | OHW dead | 3850 | DI | 15 | 10 |  |  |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 10 | 17 | DI | Rail bond applied | Energised | = | Bond applied |  | 2 | 3 | 12 | R2S3DI/12 | Rail bond applied | 3851 | DI | 15 | 11 | Y |  |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 11 | 30 | DI | Rail bond verified | Energised | = | Bond verified |  | 2 | 3 | 13 | R2S3DI/13 | Rail bond verified | 3852 | DI | 15 | 12 | Y |  |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 12 | 40 | DI | DCCB in service position | Energised | = | In Service |  | 2 | 3 | 14 | R2S3DI/14 | Racked in | 3853 | DI | 15 | 13 |  | L |  | Y | Combined with racked out
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 13 | 39 | DI | DCCB in isolated position | Energised | = | Isolated |  | 2 | 3 | 15 | R2S3DI/15 | Racked out | 3854 | DI | 15 | 14 |  | L |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 14 | 42 | DI | Remote selected | Energised | = | Remote selected |  | 2 | 3 | 16 | R2S3DI/16 | Remote | 3855 | DI | 15 | 15 | Y | - |  | Y | Combined with local
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 15 | 41 | DI | Local selected | Energised | = | Local selected |  | 2 | 3 | 17 | R2S3DI/17 | Local Ctrl | 3856 | DI | 15 | 16 | Y | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 16 | 16 | DI | Line test in progress | Energised | = | LT in progress |  | 2 | 3 | 18 | R2S3DI/18 | Line test in progress | 3857 | DI | 15 | 17 | Y | A | 10 | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 17 | 22 | DI | Line test failed | Energised | = | LT failed |  | 2 | 3 | 19 | R2S3DI/19 | Line test failed | 3858 | DI | 15 | 18 | Y | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 18 | 23 | DI | Line test passed | Energised | = | LT passed |  | 2 | 3 | 20 | R2S3DI/20 | Line test passed | 3859 | DI | 15 | 19 | Y | L |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 19 | 15 | DI | Auto reclose in progress | Energised | = | AR in progress |  | 2 | 3 | 21 | R2S3DI/21 | AR | 3860 | DI | 15 | 20 | Y | L |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 20 | 29 | DI | TCS fail alarm | Energised | = | TC Healthy |  | 2 | 3 | 22 | R2S3DI/22 | TCS | 3861 | DI | 15 | 21 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 21 | 20 | DI | DC Prot Relay Watchdog | Energised | = | Relay Healthy |  | 2 | 3 | 23 | R2S3DI/23 | DC Protection Relay | 3862 | DI | 15 | 22 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 22 | 26 | DI | CBCM watchdog alarm | Energised | = | CBCM Healthy |  | 2 | 3 | 24 | R2S3DI/24 | CBCM Fail | 3863 | DI | 15 | 23 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | S1106 | 23 | 25 | DI | Transducer watchdog alarm | Energised | = | Transducer Healthy |  | 2 | 3 | 25 | R2S3DI/25 | Transducer Fail | 3864 | DI | 15 | 24 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | [6 empty] | Low | = | Comms Healthy | [5 empty] | DC Prot Relay Comms | 38656 | DI | 151 | 0 |  | A | 10 |  | Internal to RTU
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | WORD-21 | BIT 0 | UMLe | Serial | Overcurrent trip | High | = | Fault | [5 empty] | OC TRIP | 38657 | DI | 151 | 1 |  | L
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | WORD-21 | BIT 4 | UMLe | Serial | Delta-I Relay Operated | High | = | Fault | [5 empty] | DELTA_I TRIP | 38661 | DI | 151 | 5 |  | L
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | WORD-21 | BIT 5 | UMLe | Serial | di/dt trip | High | = | Fault | [5 empty] | DI/DT TRIP | 38662 | DI | 151 | 6 |  | L
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB | 2 | WORD-21 | BIT 6 | UMLe | Serial | Protection Lockout | High | = | Locked Out | [5 empty] | LOCKOUT | 38663 | DI | 151 | 7 | Y | A
1500VDC | DCCB(HSS) | 481 | Metal clad DCCB |  | WORD-22 |  | UMLe | AI | DC Feeder Voltage +ve | 32768 | = | 2000V | [5 empty] | DCVoltage | 38912 | AI | 152 | 0 |  | A | 10 |  | High limit set to 1950V
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 |  | 1 | 12 | PO | Control +ve | [7 empty] | R1S12DO/CH4-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1150 | 2 | 13 |  | Remote Enable IT Command |  |  |  |  | 1 | 12 | 4 | R1S12DO/CH4-b | ITEnable | 3075 | PO | 12 | 3 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 |  | 3 | 10 | PO | Control +ve | [7 empty] | R1S12DO/CH3-a | [6 empty] | - |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1150 | 4 | 11 |  | Remote Disable IT Command |  |  |  |  | 1 | 12 | 3 | R1S12DO/CH3-b | ITDisable | 3074 | PO | 12 | 2 |  | - |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1151 | 6 | 21 |  | Low trip set (switch settings) | Energised | = | Low trip set |  | 2 | 6 | 8 | R2S6DI/8 | IT STATUS | 4614 | DI | 18 | 6 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1151 | 7 | 19 | DI | Intertrip scheme comms A health | Energised | = | Healthy |  | 2 | 6 | 9 | R2S6DI/9 | IT COMMS A | 4615 | DI | 18 | 7 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1151 | 8 | 20 | DI | Intertrip scheme comms B health | Energised | = | Healthy |  | 2 | 6 | 10 | R2S6DI/10 | IT COMMS B | 4616 | DI | 18 | 8 |  | A |  | Y
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1151 | 9 | X0:13 | DI | Intertrip 12V supply 1 | Energised | = | Volts present |  | 2 | 6 | 11 | R2S6DI/11 | IT PSU A FAIL | 4612 | DI | 18 | 4 |  | A |  | Y | One per interface panel
1500VDC | DCCB(HSS) | 481 | Intertrip Interface Panel | 2 | S1151 | 10 | X0:21 | DI | Intertrip 12V supply 2 | Energised | = | Volts present |  | 2 | 6 | 12 | R2S6DI/12 | IT PSU B FAIL | 4613 | DI | 18 | 5 |  | A |  | Y | One per interface panel
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 1 | 46 | DI | DCCB Open | Energised | = | Open |  | 2 | 3 | 4 | R2S3DI/4 | Status(1) | 3843 | DI | 15 | 3 |  | L |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 2 | 47 | DI | DCCB Closed | Energised | = | Closed |  | 2 | 3 | 5 | R2S3DI/5 | Status(0) | 3844 | DI | 15 | 4 |  | L |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 7 | 29 | DI | Reverse Current Trip | Energised | = | Tripped |  | 2 | 3 | 6 | R2S3DI/6 | ReverseCurrent | 3845 | DI | 15 | 5 | Y | A |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB |  | IA141 | W | 48 | AI | DC Bus Voltage +ve | 4-20mA | = | ±2000V |  | 2 | 3 | 35 | R2S3AI/CH35+ | Voltage | 3874 | AI | 15 | 34 |  | A | 10 | Y | High limit set to 1950V
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB |  | IA141 | B | 49 |  | DC Bus Voltage -ve |  |  |  |  | 2 | 3 | 35 | R2S3AI/CH35- | [6 empty] | - |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB |  | IA141 | S | 50 |  | Screen | [14 empty] | - |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 10 | 24 | DI | Busbar alive | Energised | = | Busbar not alive |  | 2 | 3 | 7 | R2S3DI/7 | DC Busbar Alive | 3846 | DI | 15 | 6 |  |  |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 13 | 40 | DI | DCCB in service position | Energised | = | In Service |  | 2 | 3 | 8 | R2S3DI/8 | Racked in | 3847 | DI | 15 | 7 |  | L |  | Y | Combined with racked out
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 14 | 39 | DI | DCCB in isolated position | Energised | = | Isolated |  | 2 | 3 | 9 | R2S3DI/9 | Racked out | 3848 | DI | 15 | 8 |  | L |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 15 | 42 | DI | Remote selected | Energised | = | Remote selected |  | 2 | 3 | 10 | R2S3DI/10 | Remote | 3849 | DI | 15 | 9 |  | - |  | Y | Combined with local
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 16 | 41 | DI | Local selected | Energised | = | Local selected |  | 2 | 3 | 11 | R2S3DI/11 | Local | 3850 | DI | 15 | 10 |  | A |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 21 | 28 | DI | TCS fail alarm | Energised | = | TC Healthy |  | 2 | 3 | 12 | R2S3DI/12 | TripCircuitSupervision | 3851 | DI | 15 | 11 |  | A |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 23 | 25 | DI | CBCM watchdog alarm | Energised | = | CBCM Healthy |  | 2 | 3 | 13 | R2S3DI/13 | CBCM Fail | 3852 | DI | 15 | 12 |  | A |  | Y
1500VDC | RDCCB | R1 DCCB | Metal clad DCCB | 2 | S1106 | 24 | 30 | DI | Transducer watchdog alarm | Energised | = | Transducer Failed |  | 2 | 3 | 14 | R2S3DI/14 | Transducer Fail | 3853 | DI | 15 | 13 | Y | A |  | Y
1500VDC | Switch | 1500V BS | 1500V BS Switch | 2 | S1160 | 1 |  | +ve | 125V dc common
1500VDC | Switch | 1500V BS | 1500V BS Switch | 2 | S1160 | 2 |  | DI | Switch Open | Energised | = | Open |  | 2 | 3 | 9 | R2S3DI/9 | Status(0) | 3848 | DI | 15 | 8 |  | A
1500VDC | Switch | 1500V BS | 1500V BS Switch | 2 | S1160 | 3 |  | DI | Switch Closed | Energised | = | Closed |  | 2 | 3 | 10 | R2S3DI/10 | Status(1) | 3849 | DI | 15 | 9 |  | A
1500VDC | Bus | 1500V BS | 1500V BS Switch | 2 | S1160 | 4 |  | DI | 1500V DC Bus 1 Live | Energised | = | Live |  | 2 | 3 | 11 | R2S3DI/11 | DC Bus 1 Live | 3850 | DI | 15 | 10 |  | A
1500VDC | Bus | 1500V BS | 1500V BS Switch | 2 | S1160 | 5 |  | DI | 1500V DC Bus 2 Live | Energised | = | Live |  | 2 | 3 | 12 | R2S3DI/12 | DC Bus 2 Live | 3851 | DI | 15 | 11 |  | A
1500VDC | Switch | 1500V Bs | 1500V BS Switch | 2 | S1160 | 6 |  | DI | Link in Service Position | Energised | = | In Service |  | 2 | 3 | 13 | R2S3DI/13 | DC Bus Link Svc Pos | 3852 | DI | 15 | 12 |  | A
1500VDC | Switch | 1500V BS | 1500V BS Switch |  | IA150 | W |  | AI | Link Switch DC Current +ve | 20mA | = | 8000A |  | 2 | 9 | 1 | R2S9AI/CH1+ | Current | 3874 | AI | 15 | 34 |  | A | 10
1500VDC | Switch | 1500V BS | 1500V BS Switch |  | IA150 | B |  |  | Link Switch DC Current +ve |  |  |  |  | 2 | 9 | 1 | R2S9AI/CH1-
1500VDC | Switch | 1500V BS | 1500V BS Switch |  | IA150 | S |  |  | Screen
1500VDC | Reactor | REACTOR | Common Equipment Panel | 1 | S4005 | 1 |  | +ve | 125V dc common | [17 empty] | No controls for reactor
1500VDC | Reactor | REACTOR | Common Equipment Panel | 1 | S4005 | 2 |  | DI | Reactor Over Pressure Trip | Energised | = | Tripped |  | 2 | 5 | 16 | R2S5DI/16 | OilOverPressure | 4367 | DI | 17 | 15 | Y | A |  | Y
1500VDC | Reactor | REACTOR | Common Equipment Panel | 1 | S4005 | 3 |  | DI | Reactor Protection Supply Healthy | Energised | = | Supply Healthy |  | 2 | 5 | 17 | R2S5DI/17 | ACSupply | 4368 | DI | 17 | 16 |  | A |  | Y
1500VDC | Reactor | REACTOR | Negative Reactor | 1 | S4006 | 1 |  | +ve | 125V dc Common | [16 empty] | Y
1500VDC | Reactor | REACTOR | Negative Reactor | 1 | S4006 | 2 |  | DI | Reactor Oil Overtemp Trip | Energised | = | Tripped |  | 2 | 5 | 18 | R2S5DI/18 | OilOverTempCritical | 4369 | DI | 17 | 17 | Y | A |  | Y
1500VDC | Reactor | REACTOR | Negative Reactor | 1 | S4006 | 3 |  | DI | Reactor Oil Overtemp Alarm | Energised | = | Healthy |  | 2 | 5 | 19 | R2S5DI/19 | OilOverTemp | 4370 | DI | 17 | 18 |  | A |  | Y
1500VDC | Reactor | REACTOR | Negative Reactor |  | IA120 | W |  | AI | Reactor Oil Temp +ve | 20mA | = | 0-150C |  | 2 | 4 | 33 | R2S4AI/CH33+ | [6 empty] | A | 10 | Y | Wired to RTU but not sent to Master Station
1500VDC | Reactor | REACTOR | Negative Reactor |  | IA120 | B |  |  | Reactor Oil Temp -ve |  |  |  |  | 2 | 4 | 33 | R2S4AI/CH33- | [8 empty] | Y
1500VDC | Reactor | REACTOR | Negative Reactor |  | IA120 | S |  |  | Screen | [16 empty] | Y
1500VDC | Reactor | REACTOR | Negative Reactor |  | IA121 | W |  | AI | Reactor Winding Temp +ve | 20mA | = | 0-150C |  | 2 | 4 | 34 | R2S4AI/CH34+ | [6 empty] | A | 10 | Y | Wired to RTU but not sent to Master Station
1500VDC | Reactor | REACTOR | Negative Reactor |  | IA121 | B |  |  | Reactor Winding Temp -ve |  |  |  |  | 2 | 4 | 34 | R2S4AI/CH34- | [8 empty] | Y
1500VDC | Reactor | REACTOR | Negative Reactor |  | IA121 | S |  |  | Screen | [16 empty] | Y
1500VDC | REC | REC | Rail Earth Contactor |  | IA130 | W |  | AI | Rail to Earth Volts +ve (Rail) | 0-20mA | = | 0-800V |  | 2 | 4 | 35 | R2S4AI/CH35+ | RailEarthVoltage | 4130 | AI | 16 | 34 |  | A | 10 | Y
1500VDC | REC | REC | Rail Earth Contactor |  | IA130 | B |  |  | Rail to Earth Volts -ve (Earth) |  |  |  |  | 2 | 4 | 35 | R2S4AI/CH35- | [8 empty] | Y
1500VDC | REC | REC | Rail Earth Contactor |  | IA130 | S |  |  | Screen | [16 empty] | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1109 | 1 |  | +ve | 125V DC Common | [16 empty] | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1109 | 2 |  | DI | Rail Earth Contactor Open | Energised | = | REC Open |  | 2 | 5 | 20 | R2S5DI/20 | Status(1) | 4371 | DI | 17 | 19 |  | A |  | Y | Normal state is open
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1109 | 3 |  | DI | Rail Earth Contactor Closed | Energised | = | REC Closed |  | 2 | 5 | 21 | R2S5DI/21 | Status(0) | 4372 | DI | 17 | 20 |  | A |  | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1109 | 4 |  | DI | Rail Earth Contactor Control Supply | Energised | = | Supply Healthy |  | 2 | 5 | 22 | R2S5DI/22 | Ctrl Supply | 4373 | DI | 17 | 21 |  | A |  | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1101 | 1 |  |  | Control +ve | [7 empty] | R1S12DO/CH4-a | [6 empty] | - |  | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1101 | 2 |  | PO | Remote Close Command |  |  |  |  | 1 | 12 | 4 | R1S12DO/CH4-b | Close | 3075 | PO | 12 | 3 |  | - |  | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1101 | 3 |  |  | Control +ve | [7 empty] | R1S12DO/CH3-a | [6 empty] | - |  | Y
1500VDC | REC | REC | Rail Earth Contactor | 1 | S1101 | 4 |  | PO | Remote Open Command |  |  |  |  | 1 | 12 | 3 | R1S12DO/CH3-b | Open | 3074 | PO | 12 | 2 |  | - |  | Y
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger | 1 | S1151 | 1 |  | +ve | 125V DC Common | [16 empty] | Y
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger | 1 | S1151 | 2 |  | DI | No1 Battery - Charger Fault | Energised | = | Charger Healthy |  | 2 | 5 | 22 | R2S5DI/22 | Fault | 4373 | DI | 17 | 21 |  | A |  | Y | Combination of all 'other' alarms
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger | 1 | S1151 | 3 |  | DI | No1 Battery – O/P Volts Low | Energised | = | Volts OK (above limit) |  | 2 | 5 | 23 | R2S5DI/23 | LowVolts | 4374 | DI | 17 | 22 |  | A |  | Y
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger | 1 | S1151 | 4 |  | DI | No1 Battery – AC Failed | Energised | = | AC Healthy |  | 2 | 5 | 24 | R2S5DI/24 | ACSupply | 4375 | DI | 17 | 23 |  | A |  | Y | Combination of ‘AC Normal’ & ’CB Open’ indications
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger |  | IA100 | W |  | AI | No1 Battery - Voltage +ve | 0-10mA | = | 0-150VDC |  | 2 | 4 | 36 | R2S4AI/CH36+ | Voltage | 4131 | AI | 16 | 35 |  | A | 10 | Y
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger |  | IA100 | B |  |  | No1 Battery - Voltage -ve |  |  |  |  | 2 | 4 | 36 | R2S4AI/CH36- | [8 empty] | Y
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger |  | IA100 | S |  |  | Screen | [16 empty] | Y
120V | BattCharger | BATTERY CHRGR 1 | 125V DC Battery Charger | 1 | S1151 | 12 |  |  | Battery Room Ventilation Fan Fail | Energised | = | Fan working |  | 2 | 5 | 25 | R2S5DI/25 | VentFan | 4376 | DI | 17 | 24 |  | A |  | Y | Required for rooms with forced ventilation
415V | AUX | AUX NO1 | 415/240V AC Board | 1 | S1150 | 1 |  | +ve | 125V DC Common | [16 empty] | Y
415V | AUX | AUX NO1 | 415/240V AC Board | 1 | S1150 | 2 |  | DI | No.1 Aux Tx In Service | Energised | = | In Service |  | 2 | 5 | 26 | R2S5DI/26 | Status | 4377 | DI | 17 | 25 |  | L |  | Y | Not required if from Rectifier Tx or 11kV Aux CB
415V | AUX | AUX NO2 | 415/240V AC Board | 1 | S1150 | 3 |  | DI | No.2 Aux Tx In Service | Energised | = | In Service |  | 2 | 5 | 27 | R2S5DI/27 | Status | 4378 | DI | 17 | 26 |  | L |  | Y | Not required if from Rectifier Tx or 11kV Aux CB
415V | AUX | AUX | 415/240V AC Board | 1 | S1150 | 4 |  | DI | Auto Selected | Energised | = | Auto |  | 2 | 5 | 28 | R2S5DI/28 | Manual Ctrl | 4379 | DI | 17 | 27 |  | A |  | Y
415V | AUX | AUX NO1 | 415/240V AC Board | 1 | S1150 | 5 |  | DI | No1 415V Healthy | Energised | = | Healthy |  | 2 | 5 | 29 | R2S5DI/29 | Supply Fail | 4380 | DI | 17 | 28 |  | A |  | Y | Not required if from Rectifier Tx or 11kV Aux CB
415V | AUX | AUX NO2 | 415/240V AC Board | 1 | S1150 | 6 |  | DI | No2 415V Healthy | Energised | = | Healthy |  | 2 | 5 | 30 | R2S5DI/30 | Supply Fail | 4381 | DI | 17 | 29 |  | A |  | Y | Not required if from Rectifier Tx or 11kV Aux CB
415V | AUX | AUX | 415/240V AC Board | 1 | S1150 | 7 |  | DI | Aux Supply Volts (C/O switch O/P) Phase Failure relay | Energised | = | Healthy |  | 2 | 5 | 31 | R2S5DI/31 | ASV | 4382 | DI | 17 | 30 |  |  |  | Y
MISC | Switch | Help Point | Help Point Button | 1 | S1179B | 1 |  | +ve | 125V DC Common | [16 empty] | Y
MISC | Switch | Help Point | Help Point Button | 1 | S1179B | 2 |  | DI | Emergency Push Button | Energised | = | Emergency |  | 1 | 4 | 14 | R1S4DI/14 | Emergency Button | 1037 | DI | 4 | 13 |  | A |  | Y | Emergency button is push on, twist off
MISC | Switch | Help Point | [15 empty] | Emergency Light on | 17153 | PO | 67 | 1 |  |  |  |  | Goes to LCR to turn emergency help point light on. One input per area.
MISC | Switch | Help Point | Help Point Light | 1 | S1176 | 1 |  | +ve | 125V DC Common | [16 empty] | Y
MISC | Switch | Help Point | Help Point Light | 1 | S1176 | 2 |  | Latch | Emergency help point light | Energised | = | Light on |  | 1 | 9 | 4 | R1S9DO/CH4 |  |  | PO | [5 empty] | Y | Hard wired output to control emergency help point light via local control programme
MISC | Staff | STAFF | Staff Switch | 1 | S1170 | 1 |  | +ve | 125V dc common | [16 empty] | Y | One input is required per area, see EL 0204559.
MISC | Staff | STAFF | Staff Switch | 1 | S1170 | 2 |  | DI | Staff access switch (Intruder Detection) | Energised | = | Staff present |  | 1 | 4 | 9 | R1S4DI/9 | Switch | 1032 | DI | 4 | 8 |  | L |  | Y
MISC | Staff | STAFF | Staff Door Reeds | 1 | S1171 | 1 |  | +ve | 125V dc common | [16 empty] | Y
MISC | Staff | STAFF | Staff Door Reeds | 1 | S1171 | 2 |  | DI | Door Reed Switches for HV Room | Energised | = | Doors Closed |  | 1 | 4 | 10 | R1S4DI/10 | DoorReed | 1033 | DI | 4 | 9 |  | L |  | Y | One input is required per area, see EL 0204559.
MISC | Staff | STAFF | [5 empty] | DI | Staff status | High | = | Staff absent | [5 empty] | Status | 16640 | DI | 65 | 0 |  | A |  |  | One per area. Internal to RTU.
MISC | SupPhone | SUPY PHONE | Bell Silence Button | 1 | S1178B | 1 |  | +ve | 125V DC Common | [16 empty] | Y
MISC | SupPhone | SUPY PHONE | Bell Silence Button | 1 | S1178B | 2 |  | DI | HV Equip Room VoIP Phone Buzzer Silence PB | Energised | = | Silence Alarm |  | 1 | 4 | 13 | R1S4DI/13 | Bell Silence | 1036 | DI | 4 | 12 | Y | L |  | Y | One input is required per area, see EL 0204559.
MISC | SupPhone | SUPY PHONE | [15 empty] | Ring | 17152 | PO | 67 | 0 |  |  |  |  | Goes to LCR to ring buzzer
MISC | SupPhone | SUPY PHONE | Piezo Buzzer | 1 | S1175 | 1 |  | +ve | 125V DC Common | [16 empty] | Y | This output is for staff alarm and phone buzzer
MISC | SupPhone | SUPY PHONE | Piezo Buzzer | 1 | S1175 | 2 |  | Latch | HV Equip Room Audible Alarm (Latched) | Energised | = | Sound Alarm |  | 1 | 9 | 3 | R1S9DO/CH3 |  |  | PO | [5 empty] | Y | Hard wired output to control staff/phone bell via local control programme
MISC | RTU | RTU | RTU Cabinet |  |  |  |  | DI | Internal RTU Fault | Low | = | Healthy | [5 empty] | Fault | 16641 | DI | 65 | 1 |  | A |  |  | Internal to RTU, for Foxboro RTUs
MISC | RTU | RTU | RTU Cabinet | 1 | Internal | 1 |  | DI | Alarm Bus Fuse | Energised | = | Healthy |  | 1 | 4 | 1 | R1S4DI/1 | Alarm Bus Fuse | 1024 | DI | 4 | 0 |  | A |  | Y
MISC | RTU | RTU | RTU Cabinet | 1 | Internal | 1 |  | DI | Remote Controls Disabled | Energised | = | Controls Disabled |  | 1 | 4 | 2 | R1S4DI/2 | Controls Disabled | 1025 | DI | 4 | 1 |  | A |  | Y | Switch in RTU, will only affect some controls
MISC | RTU | RTU | RTU Cabinet | 2 | Internal | 1 |  | DI | Control Fuse | Energised | = | Healthy |  | 1 | 4 | 3 | R1S4DI/3 | Control Bus Fuse | 1026 | DI | 4 | 2 |  | A |  | Y
COMMS | Switch | COMMS SWITCH A | C&CS switch | 1 | S1181 | 1 | K2:A1 | +ve | 48V DC Common | [16 empty] | Y
COMMS | Switch | COMMS SWITCH A | C&CS switch | 1 | S1181 | 2 | K2:A2 | DI | Comms Panel - Switch A Fault | Energised | = | Healthy |  | 1 | 4 | 4 | R1S4DI/4 | Fault | 1027 | DI | 4 | 3 |  | A |  | Y
COMMS | Switch | COMMS SWITCH B | C&CS switch | 1 | S1181 | 3 | K4:A1 | +ve | 48V DC Common | [16 empty] | Y
COMMS | Switch | COMMS SWITCH B | C&CS switch | 1 | S1181 | 4 | K4:A2 | DI | Comms Panel - Switch B Fault | Energised | = | Healthy |  | 1 | 4 | 5 | R1S4DI/5 | Fault | 1028 | DI | 4 | 4 |  | A |  | Y
COMMS | Switch | COMMS SWITCH A | Power Supply in RTU | 1 | Internal | 1 |  | DI | 125/48V DC Supply A Fail | Energised | = | Healthy |  | 1 | 4 | 6 | R1S4DI/6 | 48V Supply | 1029 | DI | 4 | 5 |  | A |  | Y
COMMS | Switch | COMMS SWITCH B | Power Supply in RTU | 1 | Internal | 1 |  | DI | 125/48V DC Supply B Fail | Energised | = | Healthy |  | 1 | 4 | 7 | R1S4DI/7 | 48V Supply | 1030 | DI | 4 | 6 |  | A |  | Y
MISC | TestCB | RTU TEST CB | RTU Cabinet | 1 | Internal | 1 |  | DI | CB Closed | Energised | = | Closed |  | 1 | 4 | 8 | R1S4DI/8 | Status | 1031 | DI | 4 | 7 |  | A |  | Y | Normally open, relay latches closed when close control sent
MISC | TestCB | RTU TEST CB | RTU Cabinet | 1 | Internal | 2 |  |  | Control +ve | [7 empty] | R1S9DO/CH1-a | [6 empty] | - |  | Y
MISC | TestCB | RTU TEST CB | RTU Cabinet | 1 | Internal | 3 |  | PO | Remote Open Command |  |  |  |  | 1 | 9 | 1 | R1S9DO/CH1-b | Open | 2304 | PO | 9 | 0 |  | - |  | Y
MISC | TestCB | RTU TEST CB | RTU Cabinet | 1 | Internal | 4 |  |  | Control +ve | [7 empty] | R1S9DO/CH2-a | [6 empty] | - |  | Y
MISC | TestCB | RTU TEST CB | RTU Cabinet | 1 | Internal | 5 |  | PO | Remote Close Command |  |  |  |  | 1 | 9 | 2 | R1S9DO/CH2-b | Close | 2305 | PO | 9 | 1 |  | - |  | Y
MISC | FIRE SYSTEM | FIRE SYSTEM | Fire Panel | 1 | S1182 | 1 |  | +ve | 125V DC Common | [16 empty] | Y | From positive alarm bus
MISC | FIRE SYSTEM | FIRE SYSTEM | Fire Panel | 1 | S1182 | 2 |  | DI | Fire Detection System Faulty | Energised | = | Healthy |  | 2 | 6 | 1 | R2S6DI/1 | Fault | 4608 | DI | 18 | 0 |  | A |  | Y | Interposing relay may be required
MISC | FIRE SYSTEM | FIRE SYSTEM | Fire Panel | 1 | S1182 | 3 |  | DI | Fire Detection System Isolated | Energised | = | Isolated |  | 2 | 6 | 2 | R2S6DI/2 | Isolated | 4609 | DI | 18 | 1 |  | A |  | Y | Interposing relay may be required
MISC | FIRE SYSTEM | FIRE SYSTEM | Fire Panel | 1 | S1182 | 4 |  | DI | Fire alarm | Energised | = | Fire detected |  | 2 | 6 | 3 | R2S6DI/3 | Fire Alarm | 4610 | DI | 18 | 2 |  | A |  | Y | Interposing relay may be required
SPARE | SPARE |  | Panel | 1 | S3000 | 15 | [20 empty] | Spare field cable core
SPARE | SPARE |  | Panel | 1 | S3000 | 16 | [20 empty] | Spare field cable core
Note on E1: The arrangement shown here is for locations with two battery systems.
Note on F1: Matthew Percival: From Cable Schedule
Note on G1: Matthew Percival: From Cable Schedule
Note on Q2: Matthew Percival: Starts at 1
Note on T2: Matthew Percival: = Master Station Slot number x 256 + Master Station Channel number
Note on V2: Matthew Percival: = (RTU Rack - 1) x 12 + Slot for physical RTU slots.
Note on W2: Matthew Percival: Starts at Zero
Note on Y2: Matthew Percival: A = the point shall alarm and log L = the point shall only log an event
Note on H118: Could be a directional relay (P127 or P14D) or a non-directional relay (P124 or P14N)
Note on H120: Could be a directional relay (P127 or P14D) or a non-directional relay (P124 or P14N)
Note on J512: Matthew Percival: Combination of stage 1, 2 and 3 overcurrent
Note on J514: Matthew Percival: Not on dc protection concept